TRANSMISSION SERVICE AGREEMENT

FOR

DEVELOPMENT AND OPERATION OF INTER-STATE TRANSMISSION SYSTEM

FOR TRANSMISSION OF ELECTRICITY THROUGH TARIFF BASED COMPETITIVE BIDDING FOR

TRANSMISSION SYSTEM FOR EVACUATION OF POWER FROM REZ IN RAJASTHAN (20GW) UNDER PHASE-III PART F

BETWEEN THE

CENTRAL TRANSMISSION UTILITY OF INDIA LIMITED

(NODAL AGENCY)

AND

Beawar Transmission Limited

September……...,2023

CONTENTS

1	Definitions and Interpretations	6

2	Effectiveness and Term of Agreement	17

3	Conditions Subsequent	19

4	Development of the Project	24

5	Construction of the Project	29

6	Connection and commissioning of the Project	34

7	Operation and Maintenance of the Project	39

8	Availability of the project	40

9	Insurances	41

10	Billing And Payment of Transmission Charges	43

11	Force Majeure	44

12	Change in Law	49

13	Events of Default and Termination	52

14	Liability and Indemnification	57

15	Assignments and Charges	63

16	Governing Law and Dispute Resolution	65

17	Representation and Warranties	67

18	Independent Engineer	69

19	Miscellaneous Provisions	71

THIS TRANSMISISON SERVICE AGREEMENT (hereinafter referred to as “TSA” or “Agreement” or "the Agreement” or “this Agreement") is made on the ………… [Insert day] of…………. [Insert month] of Two Thousand and………… [Insert Year]

BETWEEN:

The Central Transmission Utility of India Limited, "Saudamini",1st Floor, Plot No. 2, Sector-29, Gurugram-122001, Haryana acting as a Nodal Agency (referred to as the “Nodal Agency”), which expression shall unless repugnant to the context or meaning thereof include its successors, and permitted assigns) as Party of the one part;

AND

Beawar Transmission Limited, incorporated under the Companies Act, 2013, having its registered office at Core-4, Scope Complex 7, Lodhi Road Delhi, South Delhi, Delhi 110003 (herein after referred to as “Transmission Service Provider” or “TSP” or “ISTS Licensee”, which expression shall unless repugnant to the context or meaning thereof include its successors, and permitted assigns) as Party of the other part;

(“Nodal Agency” and “TSP” are individually referred to as “Party” and collectively as the “Parties”)

AND WHEREAS:

- In accordance with the Bidding Guidelines, the Bid Process Coordinator (hereinafter referred to as BPC) had initiated a competitive e-reverse bidding process through issue of RFP for selecting a Successful Bidder to build, own, operate and transfer the Project comprising of the Elements mentioned in Schedule 1 (hereinafter referred to as the Project)

- Pursuant to the said e-reverse bidding process, the BPC has identified the Successful Bidder, who will be responsible to set up the Project on build, own, operate and transfer basis to provide Transmission Service in accordance with the terms of this Agreement and the Transmission License.

- The Selected Bidder have submitted the Contract Performance Guarantee and acquired one hundred percent (100%) of the equity shareholding of Beawar Transmission Limited, along with all its related assets and liabilities in terms of the provisions of the Share Purchase Agreement.

- The TSP has agreed to make an application for a Transmission License to the Commission for setting up the Project on build, own, operate and transfer basis.

- The TSP has further agreed to make an application to the Commission for the adoption of the Transmission Charges under Section 63 of the Electricity Act, 2003, along with a certification from the Bid Evaluation Committee in accordance with the Bidding Guidelines issued by Ministry of Power, Government of India.

- The TSP has agreed to execute the agreement(s) required, if any, under Sharing Regulations within fifteen (15) days from the date of grant of Transmission License from the Commission.

- The TSP agrees to the terms and conditions laid down under Sharing Regulations, for making available the ISTS and charge the Transmission Charges in accordance with the terms and conditions of Sharing Regulations.

- The billing, collection and disbursement of the Transmission Charges by the CTU to the ISTS Licensee shall be governed as per Sharing Regulations.

- The terms and conditions stipulated in the Transmission License issued by the Commission to the TSP shall be applicable to this Agreement and the TSP agrees to comply with these terms and conditions. In case of inconsistency between the Transmission License terms & conditions and the conditions of this Agreement, the conditions stipulated in the Transmission License granted by the Commission shall prevail.

NOW, THEREFORE, IN CONSIDERATION OF THE PREMISES AND MUTUAL AGREEMENTS, COVENANTS AND CONDITIONS SET FORTH HEREIN, IT IS HEREBY AGREED BY AND BETWEEN THE PARTIES HERETO AS FOLLOWS:

ARTICLE: 1

# Definitions and Interpretations

## Definitions:

### The words / expressions used in this Agreement, unless as defined below or repugnant to the context, shall have the same meaning as assigned to them by the Electricity Act, 2003 and the rules or regulations framed there under including those issued / framed by the Commission (as defined hereunder), as amended or re-enacted from time to time or the General Clauses Act, failing which it shall bear its ordinary English meaning.

The words/expressions when used in this Agreement shall have the respective meanings as specified below:

“Acquisition Price” shall have the same meaning as defined in the Share Purchase Agreement;

“Act” or "Electricity Act" or “Electricity Act 2003” shall mean the Electricity Act, 2003 and any amendments made to the same or any succeeding enactment thereof;

“Affiliate” shall mean a company that either directly or indirectly

- controls or

- is controlled by or

- is under common control with

a Bidding Company (in the case of a single company) or a Member (in the case of a Consortium) and “control” means ownership by one entity of at least twenty-six percent (26%) of the voting rights of the other entity;

“Availability” in relation to the Project or in relation to any Element of the Project, for a given period shall mean the time in hours during that period the Project is capable to transmit electricity at its Rated Voltage and shall be expressed in percentage of total hours in the given period and shall be calculated as per the procedure contained in Appendix –II to Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations, 2019, attached herewith in Schedule 6;

“Bid” shall mean technical bid and financial bid submitted by the Bidder, in response to the RFP, in accordance with the terms and conditions of the RFP;

“Bid Deadline” shall mean the last date and time for submission of the Bid in response to RFP, as specified in the RFP;

“Bidding Company” shall refer to such single company that has made a Response to RFP for the Project;

“Bidding Consortium / Consortium” shall refer to a group of companies that has collectively made a Response to RFP for the Project;

“Bid Documents” or “Bidding Documents” shall mean the RFP, along with all attachments thereto or clarifications thereof;

“Bidding Guidelines” shall mean the “Tariff Based Competitive Bidding Guidelines for Transmission Service” and “Guidelines for Encouraging Competition in Development of Transmission Projects” issued by Government of India, Ministry of Power under Section – 63 of the Electricity Act as amended from time to time;

“Bid Process Coordinator” or “BPC” shall mean a person or its authorized representative as notified by the Government of India, responsible for carrying out the process for selection of Bidder who will acquire Transmission Service Provider;

“Bill” shall mean any bill raised by the CTU on the DICs to recover the Transmission Charges pursuant to the Sharing Regulations;

“Business Day” shall mean a day other than Sunday or a statutory holiday, on which the banks remain open for business in the State in which the Nodal Agency’s registered office is located and the concerned TSP are located;

“CEA” shall mean the Central Electricity Authority constituted under Section -70 of the Electricity Act;

“Change in law” shall have the meaning ascribed thereto in Article 12;

“Commercial Operation Date” or “COD” shall mean the date as per Article 6.2;

“Commission” or “CERC” shall mean the Central Electricity Regulatory Commission referred to   in   sub-section (1)   of Section   76   of the Electricity Act, 2003 or its successors and assigns;

“Competent Court of Law” shall mean the Supreme Court or any High Court, or any tribunal or any similar judicial or quasi-judicial body in India that has jurisdiction to adjudicate upon issues relating to the Project;

“Connection Agreement” shall mean the agreement between the CTU or STU or any other concerned parties and the TSP, setting out the terms relating to the connection of the Project to the Inter-connection Facilities and use of the Inter State Transmission System as per the provisions of the IEGC, as the case may be;

“Consultation Period” shall mean the period of sixty (60) days or such longer period as the Parties may agree, commencing from the date of issue of a TSP’s Preliminary Notice or a Nodal Agency’s Preliminary Termination Notice, as provided in Article 13 of this Agreement, for consultation between the Parties to mitigate the consequence of the relevant event having regard to all the circumstances;

“Consents, Clearances and Permits” shall mean all authorizations, licenses, approvals, registrations, permits, waivers, privileges, acknowledgements, agreements, or concessions required to be obtained from or provided by any concerned authority for the development, execution and operation of Project including without any limitation for the construction, ownership, operation and maintenance of the Transmission Lines and/or sub-stations;

“Construction Period” shall mean the period from (and including) the Effective Date of the Transmission Service Agreement up to (but not including) the COD of the Element of the Project in relation to an Element and up to (but not including) the COD of the Project in relation to the Project;

“Contractors” shall mean the engineering, procurement, construction, operation & maintenance contractors, surveyors, advisors, consultants, designers, suppliers to the TSP and each of their respective sub-contractors (and each of their respective successors and permitted assigns) in their respective capacities as such;

“Contract Performance Guarantee” shall mean the irrevocable unconditional bank guarantee, submitted and to be submitted by the TSP or by the Selected Bidder on behalf of the TSP to the Nodal Agency from a bank mentioned in Annexure 17 of the RFP, in the form attached here to as Schedule 8, in accordance with Article 3 of this Agreement and which shall include the additional bank guarantee furnished by the TSP under this Agreement;

“Contract Year”, for the purpose of payment of Transmission Charges, shall mean the period beginning on the COD, and ending on the immediately succeeding March 31 and thereafter each period of 12 months beginning on April 1 and ending on March 31 provided that the last Contract Year shall end on the last day of the term of the TSA;

“CTU” or “Central Transmission Utility” shall have same meaning as defined in the Electricity Act, 2003;

“Day” shall mean a day starting at 0000 hours and ending at 2400 hours;

“D/C” shall mean Double Circuit;

“Designated ISTS Customers” or “DICs” shall have the meaning as ascribed in the Sharing Regulations;

“Dispute” shall mean any dispute or difference of any kind between the Parties, in connection with or arising out of this Agreement including any issue on the interpretation and scope of the terms of this Agreement as provided in Article 16;

“Effective Date” for the purposes of this Agreement, shall have the same meaning as per Article 2.1 of this Agreement;

“Electrical Inspector” shall mean a person appointed as such by the Government under sub-section (1) of Section 162 of the Electricity Act 2003 and also includes Chief Electrical Inspector;

“Electricity Rules 2005” shall mean the rules framed pursuant to the Electricity Act 2003 and as amended from time to time;

“Element” shall mean each Transmission Line or each circuit of the Transmission Lines (where there are more than one circuit) or each bay of Sub-station or switching station or HVDC terminal or inverter station of the Project, including ICTs, Reactors, SVC, FSC, etc. forming part of the ISTS, which will be owned, operated and maintained by the concerned ISTS Licensee, and which has a separate Scheduled COD as per Schedule 2 of this Agreement and has a separate percentage for recovery of Transmission Charges on achieving COD as per Schedule 5 of this Agreement;

“Event of Default” shall mean the events as defined in Article 13 of this Agreement;

“Expiry Date” shall be the date which is thirty-five (35) years from the COD of the Project;

“Financial Closure” shall mean the first Business Day on which funds are made available to the TSP pursuant to the Financing Agreements;

“Financially Evaluated Entity” shall mean the company which has been evaluated for the satisfaction of the financial requirement set forth in the RFP;

“Financing Agreements” shall mean the agreements pursuant to which the TSP is to finance the Project including the loan agreements, security documents, notes, indentures, security agreements, letters of credit and other documents, as may be amended, modified, or replaced from time to time, but without in anyway increasing the liabilities of the Designated ISTS Customers / Nodal Agency;

“Financial Year” shall mean a period of twelve months at midnight Indian Standard Time (IST) between 1st April & 31st March;

“Force Majeure” and “Force Majeure Event” shall have the meaning assigned thereto in Article 11;

“GOI” shall mean Government of India;

“Grid Code” / “IEGC” shall mean the Grid Code specified by the Central Commission under Clause (h) of sub-section (1) of Section 79 of the Electricity Act;

“Independent Engineer” shall mean an agency/ company, appointed by Nodal Agency in accordance with the Guidelines for Encouraging Competition in Development of Transmission Projects.

“Indian Governmental Instrumentality” shall mean Government of India, Government of any State in India or any ministry, department, board, authority, agency, corporation, commission under the direct or indirect control of Government of India or any State Government or both, any political sub-division of any of them including any court or Commission or tribunal or judicial or quasi-judicial body in India but excluding the CTU, TSP and the Designated ISTS Customers;

“Insurances” shall mean the insurance cover to be obtained and maintained by the TSP in accordance with Article 9 of this Agreement;

“Interconnection Facilities” shall mean the facilities as may be set up for transmission of electricity through the use of the Project, on either one or both side of generating station’s / CTU’s / STU’s / ISTS Licensee’s / Designated ISTS Customer’s substations (as the case may be) which shall include, without limitation, all other transmission lines, gantries, sub-stations and associated equipments not forming part of the Project;

“ISTS Licensee” shall be the TSP under this Agreement, consequent to having been awarded a Transmission License by the CERC and shall be referred to as the TSP or the ISTS Licensee, as the context may require in this Agreement;

“Law” or “Laws” in relation to this Agreement, shall mean all laws including electricity laws in force in India and any statute, ordinance, rule, regulation, notification, order or code, or any interpretation of any of them by an Indian Governmental Instrumentality having force of law and shall include all rules, regulations, decisions and orders of the Commission;

“Lead Member of the Bidding Consortium” or “Lead Member” shall mean a company who commits at least 26% equity stake in the Project, meets the technical requirement as specified in the RFP and so designated by other Member(s) in Bidding Consortium;

“Lenders” means the banks, financial institutions, multilateral funding agencies, non banking financial companies registered with the Reserve Bank of India (RBI), insurance companies registered with the Insurance Regulatory & Development Authority (IRDA), pension funds regulated by the Pension Fund Regulatory & Development Authority (PFRDA),mutual funds registered with Securities & Exchange Board of India (SEBI), etc., including their successors and assigns, who have agreed on or before COD of the Project to provide the TSP with the debt financing described in the capital structure schedule, and any successor banks or financial institutions to whom their interests under the Financing Agreements may be transferred or assigned;

Provided that, such assignment or transfer shall not relieve the TSP of its obligations to the Nodal Agency under this Agreement in any manner and shall also does not lead to an increase in the liability of the Nodal Agency;

“Lenders Representative” shall mean the person notified by the Lender(s) in writing as being the representative of the Lender(s) or the Security Trustee and such person may from time to time be replaced by the Lender(s) pursuant to the Financing Agreements by written notice to the TSP;

“Letter of Intent” or “LOI” shall have the same meaning as in the RFP;

“Member in a Bidding Consortium / Member” shall mean each company in the Bidding Consortium;

“Month” shall mean a period of thirty (30) days from (and excluding) the date of the event;

“Monthly Transmission Charges” for any Element of the Project, after COD of the Element till COD of the Project, and for the Project after COD of the Project, shall mean the amount of Transmission Charges as specified in Schedule 5 of this Agreement multiplied by no. of days in the relevant month and divided by no. of days in the year;

“National Load Despatch Centre” shall mean the centre established as per sub-section (1) of Section 26 of the Electricity Act 2003;

“Nodal Agency” shall mean CTU, which shall execute and implement the Transmission Service Agreement (TSA);

Provided that while taking major decisions, CTU shall consult CEA on technical matters and any other matter it feels necessary.

“Notification” shall mean any notification, issued in the Gazette of India;

“Operating Period” for any Element of the Project shall mean the period from (and including) the COD of such Element of the Project, up to (and including) the Expiry Date and for the Project, shall mean the period from (and including) the COD of the Project, up to (and including) the Expiry Date;

“Parent Company” shall mean an entity that holds at least twenty-six percent (26%) of the paid - up equity capital directly or indirectly in the Bidding Company or in the Member in a Bidding Consortium, as the case may be;

“Preliminary Termination Notice” shall mean a Nodal Agency’s Preliminary Termination Notice as defined in Article 13 of this Agreement;

“Project” shall mean Transmission System for Evacuation of Power from REZ in Rajasthan (20GW) under Phase-III Part F, as detailed in Schedule 1 of this Agreement;

“Project Assets” shall mean all physical and other assets relating to and forming part of the Project including:

(a) rights over the Site for substations, ROW for transmission lines;

(b) tangible & intangible assets such as civil works and equipment including foundations, embankments, pavements, electrical systems, communication systems, relief centres, administrative offices, Sub-stations, software, tower and sub-stations designs etc;

(c) project facilities situated on the Site;

(d) all rights of the TSP under the project agreements;

(e) financial assets, such as receivables, security deposits etc;

(f) insurance proceeds; and

(g) Applicable Permits and authorisations relating to or in respect of the Transmission System;”

“Project Execution Plan” shall mean the plan referred to in Article 3.1.3(c) hereof;

“Prudent Utility Practices” shall mean the practices, methods and standards that are generally accepted internationally from time to time by electric transmission utilities for the purpose of ensuring the safe, efficient and economic design, construction, commissioning, operation, repair and maintenance of the Project and which practices, methods and standards shall be adjusted as necessary, to take account of:

  - operation, repair and maintenance guidelines given by the manufacturers to be incorporated in the Project,

  - the requirements of Law, and

  - the physical conditions at the Site;

  - the safety of operating personnel and human beings;

“Rated Voltage” shall mean voltage at which the Transmission System is designed to operate or such lower voltage at which the line is charged, for the time being, in consultation with the Central Transmission Utility;

“Rebate” shall have the meaning as ascribed to in Article 10.3 of this Agreement;

“RFP” shall mean Request for Proposal dated February 10, 2022 along with all schedules, annexures and RFP Project Documents attached thereto, issued by the BPC for tariff based competitive bidding process for selection of Bidder as TSP to execute the Project, including any modifications, amendments or alterations thereto;

“RFP Project Documents” shall mean the following documents to be entered into in respect of the Project, by the Parties to the respective agreements:

a.	Transmission Service Agreement,

b.	Share Purchase Agreement,

c.	Agreement(s) required under Sharing Regulations and

d.	Any other agreement as may be required;

“RLDC” shall mean the relevant Regional Load Dispatch Centre as defined in the Electricity Act, 2003, in the region(s) in which the Project is located;

“RPC” shall mean the relevant Regional Power Committee established by the Government of India for the specific Region(s) in accordance with the Electricity Act, 2003 for facilitating integrated operation of the Power System in that Region;

“Scheduled COD” in relation to an Element(s) shall mean the date(s) as mentioned in Schedule 2 as against such Element(s) and in relation to the Project, shall mean the date as mentioned in Schedule 2 as against such Project, subject to the provisions of Article 4.4 of this Agreement, or such date as may be mutually agreed among the Parties;

“Scheduled Outage" shall mean the final outage plan as approved by the RPC as per the provisions of the Grid Code;

“Selected Bid” shall mean the technical Bid and the Final Offer of the Selected Bidder submitted during e-reverse bidding, which shall be downloaded and attached in Schedule 7 on or prior to the Effective Date;

“Share Purchase Agreement” shall mean the agreement amongst REC Power Development and Consultancy Limited, Beawar Transmission Limited and the Successful Bidder for the purchase of one hundred (100%) per cent of the shareholding of the Beawar Transmission Limited for the Acquisition Price, by the Successful Bidder on the terms and conditions as contained therein;

“Sharing Regulations” shall mean the Central Electricity Regulatory Commission (Sharing of Inter-State Transmission Charges and Losses) Regulations, 2020 and as amended from time to time;

“Site” in relation to a substation, switching station or HVDC terminal or inverter station, shall mean the land and other places upon which such station / terminal is to be established;

“SLDC” shall mean the State Load Despatch Centre established as per sub-section (1) of Section 31 of the Electricity Act 2003;

“STU” or “State Transmission Utility” shall be the Board or the Government company, specified as such by the State Government under sub-section (1) of Section 39 of the Electricity Act 2003;

“Successful Bidder” or “Selected Bidder” shall mean the Bidder selected pursuant to the RFP and who has to acquire one hundred percent (100%) equity shares of Beawar Transmission Limited, along with all its related assets and liabilities, which will be responsible as the TSP to establish the Project on build, own, operate and transfer basis as per the terms of the TSA and other RFP Project Documents;

“TSP’s Preliminary Notice” shall mean a notice issued by the TSP in pursuant to the provisions of Article 13.3 of this Agreement;

“Target Availability” shall have the meaning as ascribed hereto in Article 8.2 of this Agreement;

“Technically Evaluated Entity” shall mean the company which has been evaluated for the satisfaction of the technical requirement set forth in RFP;

“Termination Notice” shall mean a Nodal Agency’s Termination Notice given by the Nodal Agency to the TSP pursuant to the provisions of Articles 3.3.2, 3.3.4, 4.4.2, 5.8, 13.2 and 13.3 of this Agreement for the termination of this Agreement;

“Term of Agreement” for the purposes of this Agreement shall have the meaning ascribed thereto in Article 2.2 of this Agreement;

“Transmission Charges” shall mean the Final Offer of the Selected Bidder during the e-reverse bidding and adopted by the Commission, payable to the TSP as per Sharing Regulations;

“Transmission License” shall mean the license granted by the Commission in terms of the relevant regulations for grant of such license issued under the Electricity Act;

“Transmission Service” shall mean making the Project available as per the terms and conditions of this Agreement and Sharing Regulations;

“Unscheduled Outage” shall mean an interruption resulting in reduction of the Availability of the Element(s) / Project (as the case may be) that is not a result of a Scheduled Outage or a Force Majeure Event.

“Ultimate Parent Company” shall mean an entity which owns at least twenty six percent (26%) equity in the Bidding Company or Member of a Consortium, (as the case may be) and in the Technically Evaluated Entity and / or Financially Evaluated Entity (as the case may be) and such Bidding Company or Member of a Consortium, (as the case may be) and the Technically Evaluated Entity and / or Financially Evaluated Entity (as the case may be) shall be under the direct control or indirectly under the common control of such entity;

## Interpretation:

Save where the contrary is indicated, any reference in this Agreement to:

“Agreement" shall be construed as including a reference to its Schedules, Appendices and Annexures;

"Rupee", "Rupees" and “Rs.” shall denote lawful currency of India;

“crore” shall mean a reference to ten million (10,000,000) and a “lakh” shall mean a reference to one tenth of a million (1,00,000);

"encumbrance" shall be construed as a reference to a mortgage, charge, pledge, lien or other encumbrance securing any obligation of any person or any other type of preferential arrangement (including, without limitation, title transfer and retention arrangements) having a similar effect;

"holding company" of a company or corporation shall be construed as a reference to any company or corporation of which the other company or corporation is a subsidiary;

"indebtedness" shall be construed so as to include any obligation (whether incurred as principal or surety) for the payment or repayment of money, whether present or future, actual or contingent;

"person" shall have the meaning as defined in Section 2 (49) of the Act;

"subsidiary" of a company or corporation (the holding company) shall be construed as a reference to any company or corporation:

- which is controlled, directly or indirectly, by the holding company, or

- more than half of the issued share capital of which is beneficially owned, directly or indirectly, by the holding company, or

- which is a subsidiary of another subsidiary of the holding company,

for these purposes, a company or corporation shall be treated as being controlled by another if that other company or corporation is able to direct its affairs and/or to control the composition of its board of directors or equivalent body;

"winding-up", "dissolution", "insolvency", or "reorganization" in the context of a company or corporation shall have the same meaning as defined in the Companies Act, 1956/ Companies Act, 2013 (as the case may be).

### Words importing the singular shall include the plural and vice versa.

### This Agreement itself or any other agreement or document shall be construed as a reference to this or to such other agreement or document as it may have been, or may from time to time be, amended, varied, novated, replaced or supplemented.

### A Law shall be construed as a reference to such Law including its amendments or re-enactments from time to time.

### A time of day shall, save as otherwise provided in any agreement or document be construed as a reference to Indian Standard Time.

### Different parts of this Agreement are to be taken as mutually explanatory and supplementary to each other and if there is any inconsistency between or among the parts of this Agreement, they shall be interpreted in a harmonious manner so as to give effect to each part.

### The tables of contents and any headings or sub-headings in this Agreement have been inserted for ease of reference only and shall not affect the interpretation of this Agreement.

### All interest payable under this Agreement shall accrue from day to day and be calculated on the basis of a year of three hundred and sixty-five (365) days.

### The words “hereof” or “herein”, if and when used in this Agreement shall mean a reference to this Agreement.

### The contents of Schedule 7 shall be referred to for ascertaining accuracy and correctness of the representations made by the Selected Bidder in Article 17.2.1  hereof.

ARTICLE: 2

# Effectiveness and Term of Agreement

## Effective Date:

This Agreement shall be effective from later of the dates of the following events:

- The Selected Bidder, on behalf of the TSP, has provided the Contract Performance Guarantee, as per terms of Article 3.1 of this Agreement; and

- The Selected Bidder has acquired for the Acquisition Price, one hundred percent (100%) of the equity shareholding of REC Power Development and Consultancy Limited in Beawar Transmission Limited along with all its related assets and liabilities as per the provisions of the Share Purchase Agreement. and

- The Agreement is executed and delivered by the Parties;

## Term and Termination:

### Subject to Article 2.2.3 and Article 2.4, this Agreement shall continue to be effective in relation to the Project until the Expiry Date, when it shall automatically terminate.

### Post the Expiry Date of this Agreement, the TSP shall ensure transfer of Project Assets to CTU or its successors or an agency as decided by the Central Government at zero cost and free from any encumbrance and liability. The transfer shall be completed within 90 days of expiry of this Agreement failing which CTU shall be entitled to take over the Project Assets Suo moto.

### This Agreement shall terminate before the Expiry Date in accordance with Article 13 or Article 3.3.2 or Article 3.3.4.

## Conditions prior to the expiry of the Transmission License

### In order to continue the Project beyond the expiry of the Transmission License, the TSP shall be obligated to make an application to the Commission at least two (2) years before the date of expiry of the Transmission License, seeking the Commission’s approval for the extension of the term of the Transmission License up to the Expiry Date.

### The TSP shall timely comply with all the requirements that may be laid down by the Commission for extension of the term of the Transmission License beyond the initial term of twenty-five (25) years & upto the Expiry Date and the TSP shall keep the Nodal Agency fully informed about the progress on its application for extension of the term of the Transmission License.

## Survival:

The expiry or termination of this Agreement shall not affect any accrued rights, obligations/ roles and liabilities of the Parties under this Agreement, including the right to receive liquidated damages as per the terms of this Agreement, nor shall it effect the survival of any continuing obligations/ roles for which this Agreement provides, either expressly or by necessary implication, which are to survive after the Expiry Date or termination including those under Articles 3.3.3, 3.3.5, Article 9.3 (Application of Insurance Proceeds), Article 11 (Force Majeure), Article 13 (Events of Default and Termination), Article 14 (Liability & Indemnification), Article 16 (Governing Law & Dispute Resolution), Article 19 (Miscellaneous).

## Applicability of the provisions of this Agreement

### For the purpose of Availability, Target Availability and the computation of Availability, Incentive, Penalty, the provisions provided in this Agreement shall apply and any future modifications in the relevant Rules and Regulations shall not be applicable for this Project.

### For the purposes of this Agreement for ISTS systems developed under the tariff based competitive bidding framework, the provisions relating to the definitions (Availability and COD), Article 3 (Contract Performance Guarantee and Conditions Subsequent), Article 5 (Construction of the Project), Article 6 (Connection and Commissioning of the Project), Article 8 (Target Availability and calculation of Availability), Article 11 (Force Majeure), Article 12 (Change in Law), Article 13 (Event of Default), Article 14 (Indemnification), Article 15 (Assignment and Charges), Articles 16.1, 16.2  and 16.4 (Governing Laws and Dispute Resolution) and Article 17 (representation and warranties of the ISTS Licensee) of this agreement shall supersede the corresponding provisions under Sharing Regulations.

ARTICLE: 3

# Conditions Subsequent

## Satisfaction of conditions subsequent by the TSP

### Within ten (10) days from the date of issue of Letter of Intent, the Selected Bidder, shall:

- Provide the Contract Performance Guarantee, and

- Acquire, for the Acquisition Price, one hundred percent (100%) equity shareholding of Beawar Transmission Limited from REC Power Development and Consultancy Limited, who shall sell to the Selected Bidder, the equity shareholding of Beawar Transmission Limited, along with all its related assets and liabilities.

- Execute this Agreement;

### The TSP shall, within five (5) working days from the date of acquisition of SPV by the Selected Bidder, undertake to apply to the Commission for the grant of Transmission License and for the adoption of tariff as required under section-63 of the Electricity Act.

### The Selected Bidder, on behalf of the TSP, will provide to the Central Transmission Utility of India Limited (being the Nodal Agency) the Contract Performance Guarantee for an amount of Rs. 57.60 Crore (Rupees Fifty-Seven Crore Sixty Lakhs Only).

### The Contract Performance Guarantee shall be initially valid for a period up to three (3) months after the Scheduled COD of the Project and shall be extended from time to time to be valid for a period up to three (3) months after the COD of the Project. In case the validity of the Contract Performance Guarantee is expiring before the validity specified in this Article, the TSP shall, at least thirty (30) days before the expiry of the Contract Performance Guarantee, replace the Contract Performance Guarantee with another Contract Performance Guarantee or extend the validity of the existing Contract Performance Guarantee until the validity period specified in this Article.

### The TSP agrees and undertakes to duly perform and complete the following activities within six (6) months from the Effective Date (except for c) below), unless such completion is affected due to any Force Majeure Event, or if any of the activities is specifically waived in writing by the Nodal Agency:

- To obtain the Transmission License for the Project from the Commission;

- To obtain the order for adoption of Transmission Charges by the Commission, as required under Section 63 of the Electricity Act 2003;

- To submit to the Nodal Agency, CEA & Independent Engineer, the Project Execution Plan, immediately after award of contract(s) and maximum within one hundred and twenty (120) days from the Effective Date. Also, an approved copy each of Manufacturing Quality Plan (MQP) and Field Quality Plan (FQP) would be submitted to Independent Engineer & Nodal Agency in the same time period. The TSP’s Project Execution Plan should be in conformity with the Scheduled COD as specified in Schedule 2 of this Agreement, and shall bring out clearly the organization structure, time plan and methodology for executing the Project, award of major contracts, designing, engineering, procurement, shipping, construction, testing and commissioning to commercial operation;

- To submit to the Nodal Agency, CEA & Independent Engineer a detailed bar (GANTT) chart of the Project outlining each activity (taking longer than one Month), linkages as well as durations;

- To submit to the Nodal Agency, CEA & Independent Engineer detailed specifications of conductor meeting the functional specifications specified in RFP;

- To achieve Financial Closure;

- To provide an irrevocable letter to the Lenders duly accepting and acknowledging the rights provided to the Lenders under the provisions of Article 15.3 of this Agreement and all other RFP Project Documents;

- To award the Engineering, Procurement and Construction contract (“EPC contract”) for the design and construction of the Project and shall have given to such Contractor an irrevocable notice to proceed; and

- To sign the Agreement(s) required, if any, under Sharing Regulations.

## Recognition of Lenders’ Rights by the Nodal Agency

### The Nodal Agency hereby accepts and acknowledges the rights provided to the Lenders as per Article 15.3 of this Agreement and all other RFP Project Documents.

## Consequences of non-fulfilment of conditions subsequent

### If any of the conditions specified in Article 3.1.3 is not duly fulfilled by the TSP even within three (3) Months after the time specified therein, then on and from the expiry of such period and until the TSP has satisfied all the conditions specified in Article 3.1.3, the TSP shall, on a monthly basis, be liable to furnish to  Central Transmission Utility of India Limited (being the Nodal Agency) additional Contract Performance Guarantee of Rupees Five Crore Seventy-Six Lakh Only (Rs. 5.76 Crore) within two (2) Business Days of expiry of every such Month. Such additional Contract Performance Guarantee shall be provided to Central Transmission Utility of India Limited (being the Nodal Agency) in the manner provided in Article 3.1.1 and shall become part of the Contract Performance Guarantee and all the provisions of this Agreement shall be construed accordingly. Central Transmission Utility of India Limited (being the Nodal Agency) shall be entitled to hold and / or invoke the Contract Performance Guarantee, including such additional Contract Performance Guarantee, in accordance with the provisions of this Agreement.

### Subject to Article 3.3.4, if:

- the fulfilment of any of the conditions specified in Article 3.1.3 is delayed beyond nine (9) Months from the Effective Date and the TSP fails to furnish additional Contract Performance Guarantee to the Nodal Agency in accordance with Article 3.3.1 hereof; or

- the TSP furnishes additional Performance Guarantee to the Nodal Agency in accordance with Article 3.3.1 hereof but fails to fulfil the conditions specified in Article 3.1.3 within a period of twelve (12) months from the Effective Date,

the Nodal Agency shall have the right to terminate this Agreement, by giving a Termination Notice to the TSP, in writing, of at least seven (7) days, with a copy to CEA and the Lenders’ Representative in order to enable the Lenders to exercise right of substitution in accordance with Article 15.3 of this Agreement.

### If the Nodal Agency elects to terminate this Agreement as per the provisions of Article 3.3.2, the TSP shall be liable to pay to the Nodal Agency an amount of Rs. 57.60 Crore (Rupees Fifty-Seven Crore Sixty Lakhs Only) as liquidated damages. The Nodal Agency shall be entitled to recover this amount of damages by invoking the Contract Performance Guarantee to the extent of liquidated damages, which shall be required by the Nodal Agency, and the balance shall be returned to TSP, if any.

It is clarified for removal of doubt that this Article shall survive the termination of this Agreement.

### In case of inability of the TSP to fulfil the conditions specified in Article 3.1.3 due to any Force Majeure Event, the time period for fulfilment of the condition subsequent as mentioned in Article 3.1.3, may be extended for a period of such Force Majeure Event. Alternatively, if deemed necessary, this Agreement may be terminated by the Nodal Agency by giving a Termination Notice to the TSP, in writing, of at least seven (7) days, with a copy to CEA and the Lenders’ Representative in order to enable the Lenders to exercise right of substitution in accordance with Article 15.3 of this Agreement and the Contract Performance Guarantee shall be returned as per the provisions of Article 6.5.1.

Provided, that due to the provisions of this Article 3.3.4, any increase in the time period for completion of conditions subsequent mentioned under Article 3.1.3, shall lead to an equal increase in the time period for the Scheduled COD. If the Scheduled COD is extended beyond a period of one hundred eighty (180) days due to the provisions of this Article 3.3.4, the TSP will be allowed to recover the interest cost during construction corresponding to the period exceeding one hundred eighty (180) days by adjustment in the Transmission Charges in accordance with Schedule 9.

### Upon termination of this Agreement as per Articles 3.3.2 and 3.3.4, the Nodal Agency may take steps to bid out the Project again.

### The Nodal agency, on the failure of the TSP to fulfil its obligations, if it considers that there are sufficient grounds for so doing, apart from invoking the Contract Performance Guarantee under para 3.3.3 may also initiate proceedings for blacklisting the TSP as per provisions of Article 13.2 of TSA.

## Progress Reports

The TSP shall notify the Nodal Agency and CEA in writing at least once a Month on the progress made in satisfying the conditions subsequent in Articles 3.1.3.

ARTICLE: 4

# Development of the Project

## TSP's obligations in development of the Project:

Subject to the terms and conditions of this Agreement, the TSP at its own cost and expense shall observe, comply with, perform, undertake and be responsible:

- for procuring and maintaining in full force and effect all Consents, Clearances and Permits, required in accordance with Law for development of the Project;

- for financing, constructing, owning and commissioning each of the Element of the Project for the scope of work set out in Schedule 1 of this Agreement in accordance with:

    - the Electricity Act and the Rules made thereof;

    - the Grid Code;

    - the CEA Regulations applicable, and as amended from time to time, for Transmission Lines and sub-stations:

      - the Central Electricity Authority (Technical Standards for Connectivity to the Grid) Regulations, 2007;

      - Central Electricity Authority (Technical Standards for construction of Electrical Plants and Electric Lines) Regulation, 2010;

      - Central Electricity Authority (Grid Standard) Regulations, 2010;

      - Central Electricity Authority (Safety requirements for construction, operation and maintenance of Electrical Plants and Electrical Lines) Regulation, 2011;

      - Central Electricity Authority (Measures relating to Safety and Electricity Supply) Regulation, 2010;

      - Central Electricity Authority (Technical Standards for Communication System in Power System Operation) Regulations, 2020.

    - Safety/ security Guidelines laid down by the Government;

    - Prudent Utility Practices, relevant Indian Standards and the Law;

not later than the Scheduled COD as per Schedule 2 of this Agreement;

- for entering into a Connection Agreement with the concerned parties in accordance with the Grid Code.

- for owning the Project throughout the term of this Agreement free and clear of any encumbrances except those expressly permitted under Article 15 of this Agreement;

- to co-ordinate and liaise with concerned agencies and provide on a timely basis relevant information with regard to the specifications of the Project that may be required for interconnecting the Project with the Interconnection Facilities;

- for providing all assistance to the Arbitrators as they may require for the performance of their duties and responsibilities;

- to provide to the Nodal Agency and CEA, on a monthly basis, progress reports with regard to the Project and its execution (in accordance with prescribed form) to enable the CEA to monitor and co-ordinate the development of the Project matching with the Interconnection Facilities;

- to comply with Ministry of Power order no. 25-11/6/2018 – PG dated 02.07.2020 as well as other Guidelines issued by Govt. of India pertaining to this;

- to procure the products associated with the Transmission System as per provisions of Public Procurement (Preference to Make in India) orders issued by Ministry of Power vide orders No. 11/5/2018 - Coord. dated 28.07.2020 for transmission sector, as amended from time to time read with Department for Promotion of Industry and Internal Trade (DPIIT) orders in this regard (Procuring Entity as defined in above orders shall deemed to have included Selected Bidder and/ or TSP).

Also, to comply with Department of Expenditure, Ministry of Finance vide Order (Public Procurement No 1) bearing File No. 6/18/2019-PPD dated 23.07.2020, Order (Public Procurement No 2) bearing File No. 6/18/2019-PPD dated 23.07.2020 and Order (Public Procurement No. 3) bearing File No. 6/18/2019-PPD, dated 24.07.2020, as amended from time to time, regarding public procurement from a bidder of a country, which shares land border with India;

- to submit to Nodal Agency information in the prescribed format [To be devised by Nodal Agency] for ensuring compliance to Article 4.1 i) above.

- to comply with all its obligations undertaken in this Agreement.

## Roles of the Nodal Agency in implementation of the Project:

### Subject to the terms and conditions of this Agreement, the Nodal Agency shall be the holder and administrator of this Agreement and shall inter alia:

- appoint an Independent Engineer within 90 days of the Effective Date

- provide letters of recommendation to the concerned Indian Governmental Instrumentality, as may be requested by the TSP from time to time, for obtaining the Consents, Clearances and Permits required for the Project;

- coordinate among TSP and upstream/downstream entities   in respect of Interconnection Facilities; and

- monitor the implementation of the Agreement and take appropriate action for breach thereof including revocation of guarantees, cancellation of Agreement, blacklisting etc

- provide all assistance to the Arbitrators as required for the performance of their duties and responsibilities; and

- perform any other responsibility (ies) as specified in this Agreement.

## Time for Commencement and Completion:

- The TSP shall take all necessary steps to commence work on the Project from the Effective Date of the Agreement and shall achieve Scheduled COD of the Project in accordance with the time schedule specified in Schedule 2 of this Agreement;

- The COD of each Element of the Project shall occur no later than the Scheduled COD or within such extended time to which the TSP shall be entitled under Article 4.4 hereto.

## Extension of time:

### In the event that the TSP is unable to perform its obligations for the reasons solely attributable to the Nodal Agency, the Scheduled COD shall be extended, by a ‘day to day’ basis, subject to the provisions of Article 13.

### In the event that an Element or the Project cannot be commissioned by its Scheduled COD on account of any Force Majeure Event as per Article 11, the Scheduled COD shall be extended, by a ‘day to day’ basis for a period of such Force Majeure Event.  Alternatively, if deemed necessary, the Nodal Agency may terminate the Agreement as per the provisions of Article 13.4 by giving a Termination Notice to the TSP, in writing, of at least seven (7) days, with a copy to CEA and the Lenders’ Representative in order to enable the Lenders to exercise right of substitution in accordance with Article 15.3 of this Agreement.

### If the Parties have not agreed, within thirty (30) days after the affected Party’s performance has ceased to be affected by the relevant circumstance, on how long the Scheduled COD should be deferred by, any Party may raise the Dispute to be resolved in accordance with Article 16.

## Metering Arrangements:

### The TSP shall comply with all the provisions of the IEGC and the Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006 as amended from time to time, with regard to the metering arrangements for the Project. The TSP shall fully cooperate with the CTU / STU / RLDC and extend all necessary assistance in taking meter readings.

## Interconnection Facilities:

### Subject to the terms and conditions of this Agreement, the TSP shall be responsible for connecting the Project with the interconnection point(s) specified in Schedule 1 of this Agreement. The Interconnection Facilities shall be developed as per the scope of work and responsibilities assigned in Schedule 1 of this Agreement. The Nodal Agency shall be responsible for coordinating to make available the Interconnection Facilities.

### In order to remove any doubts, it is made clear that the obligation of the TSP within the scope of the project is to construct the Project as per Schedule-1 of this Agreement and in particular to connect it to the Interconnection Facilities as specified in this Agreement.

ARTICLE: 5

# Construction of the Project

## TSP’s Construction Responsibilities:

### The TSP, at its own cost and expense, shall be responsible for designing, constructing, erecting, testing and commissioning each Element of the Project by the Scheduled COD in accordance with the Regulations and other applicable Laws specified in Article 4.1 of this Agreement.

### The TSP acknowledges and agrees that it shall not be relieved from any of its obligations under this Agreement or be entitled to any extension of time or any compensation whatsoever by reason of the unsuitability of the Site or Transmission Line route(s).

### The TSP shall be responsible for obtaining all Consents, Clearances and Permits related but not limited to road / rail / river / canal / power line / crossings, Power and Telecom Coordination Committee (PTCC), defence, civil aviation, right of way / way-leaves and environmental & forest clearances from relevant authorities required for developing, financing, constructing, maintaining/ renewing all such Consents, Clearances and Permits in order to carry out its obligations under this Agreement in general and shall furnish to the Nodal Agency such copy/ies of each Consents, Clearances and Permits, on demand. Nodal Agency shall provide letters of recommendation to the concerned Indian Governmental Instrumentality, as may be requested by the TSP from time to time, for obtaining the Consents, Clearances and Permits required for the Project.

### The TSP shall be responsible for:

### acquisition of land for location specific substations, switching stations or HVDC terminal or inverter stations. Also, the actual location of Greenfield substations (Switching Stations or HVDC Terminal or Inverter Stations) for a generation pooling substation and for load serving substations in the scope of TSP shall not be beyond 3 Km radius of the location proposed by the BPC in the survey report. However, actual location of any Greenfield Intermediate Substations in the scope of TSP shall not be beyond 10 Km radius of the location proposed by the BPC in the Survey Report.

### final selection of Site including its geo-technical investigation;

### survey and geo-technical investigation of line route in order to determine the final route of the Transmission Lines;

### seeking access to the Site and other places where the Project is being executed, at its own risk and costs, including payment of any crop, tree compensation or any other compensation as may be required.

### In case the Project involves any resettlement and rehabilitation, the resettlement and rehabilitation package will be implemented by the State Government authorities, for which the costs are to be borne by the TSP and no changes would be allowed in the Transmission Charges on account of any variation in the resettlement and rehabilitation cost. The TSP shall provide assistance on best endeavour basis, in implementation of the resettlement and rehabilitation package, if execution of such package is in the interest of expeditious implementation of the Project and is beneficial to the Project affected persons.

## Appointing Contractors:

### The TSP shall conform to the requirements as provided in this Agreement while appointing Contractor(s) for procurement of goods & services.

### The appointment of such Contractor(s) shall neither relieve the TSP of any of its obligations under this Agreement nor make the Nodal Agency liable for the performance of such Contractor(s).

## Monthly Progress Reporting:

The TSP shall provide to the CEA, Nodal Agency & Independent Engineer, on a monthly basis, progress reports along with likely completion date of each Element with regard to the Project and its execution (in accordance with prescribed form). The Nodal Agency/ CEA shall monitor the development of the Project for its timely completion for improving and augmenting the electricity system as a part of its statutory responsibility.

## Quality of Workmanship:

The TSP shall ensure that the Project is designed, built and completed in a good workmanship using sound engineering and construction practices, and using only materials and equipment that are new and manufactured as per the MQP and following approved FQP for erection, testing & commissioning and complying with Indian /International Standards such that, the useful life of the Project will be at least thirty-five (35) years from the COD of the Project.

The TSP shall ensure that all major substation equipment / component (e.g. transformers, reactors, Circuit Breakers, Instrument Transformers (IT), Surge Arresters (SA), Protection relays, clamps & connectors etc.), equipment in terminal stations of HVDC installations including Thyristor/ IGBT valves, Converter Transformers, smoothing reactors, Transformer bushings and wall bushings, GIS bus ducts, towers and gantry structures and transmission towers or poles and line materials (conductors, earthwire, OPGW, insulator, accessories for conductors, OPGW & earthwires, hardware fittings for insulators, aviation lights etc), facilities and system shall be designed, constructed and tested (Type test, Routine tests, Factory Acceptance Test (FAT)) in accordance with relevant CEA Regulations and Indian Standards. In case Indian Standards for any particular equipment/ system/ process is not available, IEC/ IEEE or equivalent International Standards and Codes shall be followed.

## Progress Monitoring & Quality Assurance:

### The Project Execution Plan submitted by the TSP in accordance with Article 3.1.3 c) shall comprise of detailed schedule of all the equipments/items /materials required for the Project, right from procurement of raw material till the dispatch from works and receipt at the site. Further, it should also include various stages of the construction schedule up to the commissioning of the Project.

### Nodal Agency, CEA & Independent Engineer shall have access at all reasonable times to the Site and to the Manufacturer’s works and to all such places where the Project is being executed.

### Independent Engineer shall ensure conformity of the conductor specifications with the functional specifications specified in RFP.

### The Independent Engineer shall monitor the following during construction of the Project:

- Quality of equipments, material, foundation, structures and workmanship etc. as laid down in Article 5.4 and 6.1.4 of the TSA. Specifically, quality of Sub-station equipments, transmission line material and workmanship etc. would be checked in accordance with the Article 5.4.

- Progress in the activities specified in Condition Subsequent

- Verification of readiness of the elements including the statutory clearances & completion of civil works, fixing of all components and finalisation of punch points (if any) prior to charging of the elements

- Progress of construction of substation and Transmission Lines

5.5.5 	The progress shall be reviewed by the Independent Engineer against the Project Execution Plan. The Independent Engineer shall prepare its report on monthly basis and submit the same to Nodal Agency highlighting the progress achieved till the end of respective month vis-à-vis milestone activities, areas of concern, if any, which may result in delay in the timely completion of the Project. Based on the progress, Nodal Agency and/ or CEA shall issue written instructions to the TSP to take corrective measures, as may be prudent for the timely completion of the Project. In case of any deficiency, the Nodal Agency would be at liberty to take action in accordance with the procedure of this Agreement.

5.5.6 	For any delay in commissioning any critical Element(s), as identified in Schedule 1 & Schedule 2 of this Agreement, beyond a period of 45 days shall lead to a sequestration of 10% of the Contract Performance Guarantee.

## Site regulations and Construction Documents

The TSP shall abide by the Safety Rules and Procedures as mentioned in Schedule 3 of this Agreement

The TSP shall retain at the Site and make available for inspection at all reasonable times, copies of the Consents, Clearances and Permits, construction drawings and other documents related to construction.

## Supervision of work:

The TSP shall provide all necessary superintendence for execution of the Project and its supervisory personnel shall be available to provide full-time superintendence for execution of the Project. The TSP shall provide skilled personnel who are experienced in their respective fields.

## Remedial Measures:

The TSP shall take all necessary actions for remedying the shortfall in achievement of timely progress in execution of the Project, if any, as intimated by the Independent Engineer and/ or CEA and/ or the Nodal Agency. However, such intimation by the Independent Engineer and/ or CEA and/ or the Nodal Agency and the subsequent effect of such remedial measures carried out by the TSP shall not relieve the TSP of its obligations in the Agreement. Independent Engineer and/ or CEA and/ or the Nodal Agency may carry out random inspections during the Project execution, as and when deemed necessary by it. If the shortfalls as intimated to the TSP are not remedied to the satisfaction of the CEA and/ or the Nodal Agency, this Agreement may be terminated by the Nodal Agency by giving a Termination Notice to the TSP, in writing, of at least seven (7) days, with a copy to CEA and the Lenders’ Representative in order to enable the Lenders to exercise right of substitution in accordance with Article 15.3 of this Agreement.

ARTICLE: 6

# Connection and commissioning of the Project

## Connection with the Inter-Connection Facilities:

### The TSP shall give the RLDC(s), CTU, / STU, as the case may be, and any other agencies as required, at least sixty (60) days advance written notice of the date on which it intends to connect an Element of the Project, which date shall not be earlier than its Scheduled COD or Schedule COD extended as per Article 4.4.1 & 4.4.2 of this Agreement, unless mutually agreed to by Parties. Further, any preponing of COD of any element prior to Scheduled COD must be approved by the Nodal Agency.

### The RLDC / SLDC (as the case may be) or the CTU / STU (as the case may be), for reasonable cause, including non-availability of   Interconnection Facilities as per Article 4.2, can defer the connection for up to fifteen (15) days from the date notified by the TSP pursuant to Article 6.1.1, if it notifies to the TSP in writing, before the date of connection, of the reason for the deferral and when the connection is to be rescheduled.  However, no such deferment on one or more occasions would be for more than an aggregate period of thirty (30) days.  Further, the Scheduled COD would be extended as required, for all such deferments on “day to day” basis.

### Subject to Articles 6.1.1 and 6.1.2, any Element of Project may be connected with the Interconnection Facilities when:

- it has been completed in accordance with this Agreement and the Connection Agreement;

- it meets the Grid Code, Central Electricity Authority (Technical Standards for Connectivity to the Grid) Regulations, 2007 as amended from time to time and all other Indian legal requirements, and

- The TSP has obtained the approval in writing of the Electrical Inspector certifying that the Element is ready from the point of view of safety of supply and can be connected with the Interconnection Facilities.

- It has satisfactorily met all the testing requirements as per Articles 6.1.4

### Site Acceptance Test (SAT)/ pre-commissioning tests of all major substation equipment, component, system, facilities shall be successfully carried out before commissioning. The Type tests, FAT and SAT reports should be available at the substation / terminal station of HVDC installations for ready reference of operation and maintenance staff and has to be made available to the Independent Engineer appointed for quality monitoring or their authorised representatives, as and when they wish to examine the same.

## Commercial Operation:

### An Element of the Project shall be declared to have achieved COD twenty-four (24) hours following the connection of the Element with the Interconnection Facilities pursuant to Article 6.1 or seven (7) days after the date on which it is declared by the TSP to be ready for charging but is not able to be charged for reasons not attributable to the TSP subject to Article 6.1.2.

Provided that an Element shall be declared to have achieved COD only after all the Element(s), if any, which are pre-required to have achieved COD as defined in Schedule 2 of this Agreement, have been declared to have achieved their respective COD.

### Once any Element of the Project has been declared to have achieved deemed COD as per Article 6.2.1 above, such Element of the Project shall be deemed to have Availability equal to the Target Availability till the actual charging of the Element and to this extent, TSP shall be eligible for the Monthly Transmission Charges applicable for such Element

## Compensation for Direct Non Natural Force Majeure Event or Indirect Non Natural Force Majeure Event or Natural Force Majeure Event (affecting the Nodal Agency)

### If the TSP is otherwise ready to connect the Element(s) of the Project  and has given due notice, as per provisions of Article 6.1.1, to the concerned agencies of the date of intention to connect the Element(s) of the Project, where such date is not before the Scheduled COD, but is not able to connect the Element(s) of the Project by the said date specified in the notice, due to Direct Non Natural Force Majeure Event or Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the  Nodal Agency, provided such Direct Non Natural Force Majeure Event or Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the  Nodal Agency has continued for a period of more than three (3) continuous or non-continuous Months, the TSP shall, until the effects of the Direct Non Natural Force Majeure Event or of Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the  Nodal Agency no longer prevent the TSP from connecting the Element(s) of the Project, be deemed to have achieved COD relevant to that date and to this extent, be deemed to have been providing Transmission Service with effect from the date notified, and shall be treated as follows:

- In case of delay due to Direct Non Natural Force Majeure Event, TSP is entitled for Transmission Charges calculated on Target Availability for the period of such events in excess of three (3) continuous or non continuous Months in the manner provided in (c) below.

- In case of delay due to Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the Nodal Agency, TSP is entitled for payment for debt service which is due under the Financing Agreements, subject to a maximum of Transmission Charges calculated on Target Availability, for the period of such events in excess of three (3) continuous or non continuous Months in the manner provided in (c) below.

- In case of delay due to Direct Non Natural Force Majeure Event or Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the Nodal Agency, the TSP is entitled for payments mentioned in (a) and (b) above, after commencement of Transmission Service, in the form of an increase in Transmission Charges. These amounts shall be paid from the date, being the later of a) the date of cessation of such Indirect Non Natural Force Majeure Event or Natural Force Majeure Event affecting the Nodal Agency and b) the completion of sixty (60) days from the receipt of the Financing Agreements by the Nodal Agency from the TSP.

Provided such increase in Transmission Charges shall be so as to put the TSP in the same economic position as the TSP would have been in case the TSP had been paid amounts mentioned in (a) and (b) above in a situation where the Force Majeure Event had not occurred.

For the avoidance of doubt, it is clarified that the charges payable under this Article 6.3.1 shall be recovered as per Sharing Regulations.

## Liquidated Damages for Delay in achieving COD of Project:

### If the TSP fails to achieve COD of any Element of the Project or the Project, by the Element’s / Project’s Scheduled COD or such Scheduled COD as extended under Articles 4.4.1 and 4.4.3, then the TSP shall pay to the  Nodal Agency, a sum equivalent to 3.33% of Monthly Transmission Charges  applicable for the Element of the Project [in case where no Elements have been defined, to be on the Project as a whole] / Project, for each day of delay up to sixty (60) days of delay and beyond that time limit, at the rate of five percent (5%) of the Monthly Transmission Charges applicable to such Element / Project, as liquidated damages for such delay and not as penalty, without prejudice to any rights of the Nodal Agency under the Agreement.

### The TSP’s maximum liability under this Article 6.4 shall be limited to the amount of liquidated damages calculated in accordance with Article 6.4.1 for and up to six (6) months of delay for the Element or the Project.

Provided that, in case of failure of the TSP to achieve COD of the Element of the Project even after the expiry of six (6) months from its Scheduled COD, the provisions of Article 13 shall apply.

### The TSP shall make payment to the Nodal Agency of the liquidated damages calculated pursuant to Article 6.4.1 within ten (10) days of the earlier of:

- the date on which the applicable Element achieves COD; or

- the date of termination of this Agreement.

The payment of such damages shall not relieve the TSP from its obligations to complete the Project or from any other obligation and liabilities under the Agreement.

### If the TSP fails to pay the amount of liquidated damages to the Nodal Agency within the said period of ten (10) days, the Nodal Agency shall be entitled to recover the said amount of the liquidated damages by invoking the Contract Performance Guarantee. If the then existing Contract Performance Guarantee is for an amount which is less than the amount of the liquidated damages payable by the TSP to the Nodal Agency under this Article 6.3 and  the TSP fails to make payment of the balance amount of the liquidated damages not covered by the Contract Performance Guarantee, then such balance amount shall be deducted  from the Transmission Charges payable to the TSP. The right of the Nodal Agency to encash the Contract Performance Guarantee is without prejudice to the other rights of the Nodal Agency under this Agreement.

### For avoidance of doubt, it is clarified that amount payable by TSP under this Article is over and above the penalty payable by TSP under Article 5.5.6 of this Agreement.

## Return of Contract Performance Guarantee

### The Contract Performance Guarantee as submitted by TSP in accordance with Article 3.1.1 shall be released by the Nodal Agency within three (3) months from the COD of the Project.  In the event of delay in achieving Scheduled COD of any of the Elements by the TSP (otherwise than due to reasons as mentioned in Article 3.1.3 or Article 11) and consequent part invocation of the Contract Performance Guarantee by the Nodal Agency, Nodal Agency shall release the Contract Performance Guarantee, if any remaining unadjusted, after the satisfactory completion by the TSP of all the requirements regarding achieving the Scheduled COD of the remaining Elements of the Project.  It is clarified that the Nodal Agency shall also return / release the Contract Performance Guarantee in the event of (i) applicability of Article 3.3.2 to the extent the Contract Performance Guarantee is valid for an amount in excess of Rs. 57.60 Crore (Rupees Fifty-Seven Crore Sixty Lakhs Only), or (ii) termination of this Agreement by the Nodal Agency as mentioned under Article 3.3.4 of this Agreement.

### The release of the Contract Performance Guarantee shall be without prejudice to other rights of the Nodal Agency under this Agreement.

ARTICLE: 7

# Operation and Maintenance of the Project

## Operation and Maintenance of the Project:

## The TSP shall be responsible for ensuring that the Project is operated and maintained in accordance with the regulations made by the Commission and CEA from time to time and provisions of the Act.

ARTICLE: 8

# Availability of the project

## Calculation of Availability of the Project:

Calculation of Availability for the Elements and for the Project, as the case may be, shall be as per Appendix –II to Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations, 2019, as applicable on the Bid Deadline and as appended in Schedule 6 of this Agreement.

## Target Availability:

The Target Availability of each Element and the Project shall be 98%.

Payment of monthly Transmission charges based on actual availability will be calculated as per para 1.2 of Schedule 4 of this Agreement.

If the availability of any Element or the Project is below the Target Availability, for six consecutive months in a Contract Year, the DIC(s) or the Nodal Agency may issue a show cause notice to the TSP, asking them to show cause as to why the Transmission Service Agreement be not terminated, and if no satisfactory cause is shown it may terminate the Agreement. If the Nodal Agency is of the opinion that the transmission system is of critical importance, it may carry out or cause to carry the operation and maintenance of transmission system at the risk and cost of TSP.

ARTICLE: 9

# Insurances

## Insurance:

### The TSP shall effect and maintain or cause to be effected and maintained during the Construction Period and the Operating Period, adequate Insurances against such risks, with such deductibles including but not limited to any third party liability and endorsements and co-beneficiary/insured, as may be necessary under

- any of the Financing Agreements,

- the Laws, and

- in accordance with Prudent Utility Practices.

### The Insurances shall be taken effective from a date prior to the date of the Financial Closure till the Expiry Date.

## Evidence of Insurance cover:

### The TSP shall furnish to the Nodal Agency copies of certificates and policies of the Insurances, as and when the Nodal Agency may seek from the TSP as per the terms of Article 9.1

## Application of Insurance Proceeds:

### Save as expressly provided in this Agreement, the policies of Insurances and the Financing Agreements, the proceeds of any insurance claim made due to loss or damage to the Project or any part of the Project shall be first applied to reinstatement, replacement or renewal of such loss or damage.

### If a Natural Force Majeure Event renders the Project no longer economically and technically viable and the insurers under the Insurances make payment on a “total loss” or equivalent basis, the portion of the proceeds of such Insurance available to the TSP (after making admissible payments to the Lenders as per the Financing Agreements) shall be allocated only to the TSP. Nodal Agency and / or concerned Designated ISTS Customers shall have no claim on such proceeds of the Insurance.

### Subject to the requirements of the Lenders under the Financing Agreements, any dispute or difference between the Parties as to whether the Project is no longer economically and technically viable due to a Force Majeure Event or whether that event was adequately covered in accordance with this Agreement by the Insurances shall be determined in accordance with Article 16.

## Effect on liability of the Nodal Agency / Designated ISTS Customers

### The Nodal Agency and / or the Designated ISTS Customers shall have no financial obligations or liability whatsoever towards the TSP in respect of this Article 9.

### ARTICLE: 10

# Billing And Payment of Transmission Charges

## Subject to provisions of this Article 10, the Monthly Transmission Charges shall be paid to the TSP, in Indian Rupees, on monthly basis as per the provisions of the Sharing Regulations, from the date on which an Element(s) has achieved COD until the Expiry Date of this Agreement, unless terminated earlier and in line with the provisions of Schedule 4 of this Agreement.

## Calculation of Monthly Transmission Charges:

The Monthly Transmission Charges for each Contract Year including Incentive & Penalty payment shall be calculated in accordance with the provisions of Schedule 4 of this Agreement.

## Rebate & Late Payment Surcharge:

### The rebate and late payment surcharge shall be governed as per Sharing Regulations.

## Disputed Bills, Default in payment by the Designated ISTS Customers & Annual Reconciliation:

### Any Disputed Bill, Default in payment by the Designated ISTS Customers & Annual Reconciliation shall be governed as per Sharing Regulations.

ARTICLE: 11

# Force Majeure

## Definitions

### The following terms shall have the meanings given hereunder.

## Affected Party

### An Affected Party means any Party whose performance has been affected by an event of Force Majeure.

### Any event of Force Majeure shall be deemed to be an event of Force Majeure affecting the TSP only if the Force Majeure event affects and results in, late delivery of machinery and equipment for the Project or construction, completion, commissioning of the Project by Scheduled COD and/or operation thereafter;

## Force Majeure

A ‘Force Majeure’ means any event or circumstance or combination of events and circumstances including those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations/ roles under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices:

### Natural Force Majeure Events:

- act of God, including, but not limited to drought, fire and explosion (to the extent originating from a source external to the Site), earthquake, volcanic eruption, landslide, flood, cyclone, typhoon, tornado, or exceptionally adverse weather conditions, which are in excess of the statistical measures for the last hundred (100) years; and

- epidemic/ pandemic notified by Indian Governmental Instrumentality.

### Non-Natural Force Majeure Events :

### Direct Non–Natural Force Majeure Events

### Nationalization or compulsory acquisition by any Indian Governmental Instrumentality of any material assets or rights of the Affected Party; or

### the unlawful, unreasonable or discriminatory revocation of, or refusal to renew, any Consents, Clearances and Permits required by the Affected Party to perform their obligations/ roles under the RFP Project Documents or any unlawful, unreasonable or discriminatory refusal to grant any other Consents, Clearances and Permits required for the development/ operation of the Project, provided that a Competent Court of Law declares the revocation or refusal to be unlawful, unreasonable and discriminatory and strikes the same down; or

### any other unlawful, unreasonable or discriminatory action on the part of an Indian Governmental Instrumentality which is directed against the Project, provided that a Competent Court of Law declares the action to be unlawful, unreasonable and discriminatory and strikes the same down.

### Indirect Non - Natural Force Majeure Events

### act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action; or

### radio active contamination or ionising radiation originating from a source in India or resulting from any other Indirect Non Natural Force Majeure Event mentioned above, excluding circumstances where the source or cause of contamination or radiation is brought or has been brought into or near the Site by the Affected Party or those employed or engaged by the Affected Party; or

### industry-wide strikes and labour disturbances, having a nationwide impact in India.

## Force Majeure Exclusions

### Force Majeure shall not include (i) any event or circumstance which is within the reasonable control of the Parties and (ii) the following conditions, except to the extent that they are consequences of an event of Force Majeure:

### Unavailability, late delivery, or changes in cost of the machinery, equipment, materials, spare parts etc. for the Project;

### Delay in the performance of any Contractors or their agents;

### Non-performance resulting from normal wear and tear typically experienced in transmission materials and equipment;

### Strikes or labour disturbance at the facilities of the Affected Party;

### Insufficiency of finances or funds or the Agreement becoming onerous to perform; and

### Non-performance caused by, or connected with, the Affected Party’s:

### negligent or intentional acts, errors or omissions;

### failure to comply with an Indian Law; or

### breach of, or default under this Agreement or any Project    Documents.

### Any error or omission in the survey report provided by BPC during the bidding process.

## Notification of Force Majeure Event

### The Affected Party shall give notice to the other Party of any event of Force Majeure as soon as reasonably practicable, but not later than seven (7) days after the date on which such Party knew or should reasonably have known of the commencement of the event of Force Majeure.  If an event of Force Majeure results in a breakdown of communications rendering it unreasonable to give notice within the applicable time limit specified herein, then the Party claiming Force Majeure shall give such notice as soon as reasonably practicable after reinstatement of communications, but not later than one (1) day after such reinstatement.

### Provided that, such notice shall be a pre-condition to the Affected Party’s entitlement to claim relief under this Agreement. Such notice shall include full particulars of the event of Force Majeure, its effects on the Party claiming relief and the remedial measures proposed. The Affected Party shall give the other Party regular reports on the progress of those remedial measures and such other information as the other Party may reasonably request about the Force Majeure.

### The Affected Party shall give notice to the other Party of (i) the cessation of the relevant event of Force Majeure; and (ii) the cessation of the effects of such event of Force Majeure on the performance of its rights or obligations/ roles under this Agreement, as soon as practicable after becoming aware of each of these cessations.

## Duty to perform and duty to mitigate

### To the extent not prevented by a Force Majeure Event, the Affected Party shall continue to perform its obligations/ roles as provided in this Agreement. The Affected Party shall use its reasonable efforts to mitigate the effect of any event of Force Majeure as soon as practicable.

## Available Relief for a Force Majeure Event

### Subject to this Article 11,

### no Party shall be in breach of its obligations/ roles pursuant to this Agreement to the extent that the performance of its obligations/ roles was prevented, hindered or delayed due to a Force Majeure Event;

### each Party shall be entitled to claim relief for a Force Majeure Event affecting its performance in relation to its obligations/ roles under Articles 3.3.4, 4.4.2 and 6.3.1 of this Agreement.

### For the avoidance of doubt, it is clarified that the computation of Availability of the Element(s) under outage due to Force Majeure Event, as per Article 11.3  affecting the TSP shall be as per Appendix –II to Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations, 2019 as on  Bid Deadline. For the event(s) for which the Element(s) is/are deemed to be available as per Appendix –II to Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations, 2019, then the Transmission Charges, as applicable to such Element(s), shall be payable as per Schedule 4, for the duration of such event(s).

### For so long as the TSP is claiming relief due to any Force Majeure Event under this Agreement, the Nodal Agency may, if it so desires, from time to time on one (1) day notice, inspect the Project and the TSP shall provide the Nodal Agency’s personnel with access to the Project to carry out such inspections.

### For avoidance of doubt, the TSP acknowledges that for extension of Scheduled COD a period up to one hundred eighty (180) days due to Force Majeure event, no compensation on the grounds such as interest cost, incident expenditure, opportunity cost will be made to the TSP. However, if Scheduled COD is extended beyond a period of one hundred eighty (180) days due to Force Majeure event, the TSP will be allowed to recover the interest cost during construction corresponding to the period exceeding one hundred eighty (180) days by adjustment in the Transmission Charges in accordance with Schedule 9.

ARTICLE: 12

# Change in Law

## Change in Law

### Change in Law means the occurrence of any of the following after the Bid Deadline resulting into any additional recurring / non-recurring expenditure by the TSP or any savings of the TSP:

  - the enactment, coming into effect, adoption, promulgation, amendment, modification or repeal (without re-enactment or consolidation) in India, of any Law, including rules and regulations framed pursuant to such Law, subject to the provisions under Article 12.1.2;

  - a change in the interpretation or application of any Law by any Indian Governmental Instrumentality having the legal power to interpret or apply such Law, or any Competent Court of Law;

  - the imposition of a requirement for obtaining any Consents, Clearances and Permits which was not required earlier;

  - a change in the terms and conditions prescribed for obtaining any Consents, Clearances and Permits or the inclusion of any new terms or conditions for obtaining such Consents, Clearances and Permits;

  - any change in the licensing regulations of the Commission, under which the Transmission License for the Project was granted if made applicable by such Commission to the TSP;

  - change in wind zone; or

  - any change in tax or introduction of any tax made applicable for providing Transmission Service by the TSP as per the terms of this Agreement.

### Notwithstanding anything contained in this Agreement, Change in Law shall not cover any change:

  - Taxes on corporate income; and

  - Withholding tax on income or dividends distributed to the shareholders of the TSP.

## Relief for Change in Law

### During Construction Period, the impact of increase/decrease in the cost of the Project on the Transmission Charges shall be governed by the formula given in Schedule 9 of this Agreement.

### During the Operation Period:

During the operation period, if as a result of Change in Law, the TSP suffers or is benefited from a change in costs or revenue, the aggregate financial effect of which exceeds 0.30% (zero point three percent) of the Annual Transmission Charges in aggregate for a Contract Year, the TSP may notify so to the Nodal Agency and propose amendments to this Agreement so as to place the TSP in the same financial position as it would have enjoyed had there been no such Change in Law resulting in change in costs or revenue as aforesaid.

### For any claims made under Articles 12.2.1 and 12.2.2 above, the TSP shall provide to the Nodal Agency documentary proof of such increase / decrease in cost of the Project / revenue for establishing the impact of such Change in Law.

### In cases where Change in Law results in decrease of cost and it comes to the notice of Nodal Agency that TSP has not informed Nodal Agency about such decrease in cost, Nodal Agency may initiate appropriate claim.

## Notification of Change in Law:

### If the TSP is affected by a Change in Law in accordance with Article 12.1 and wishes to claim relief for such Change in Law under this Article 12, it shall give notice to Nodal Agency of such Change in Law as soon as reasonably practicable after becoming aware of the same.

### The TSP shall also be obliged to serve a notice to the Nodal Agency even when it is beneficially affected by a Change in Law.

### Any notice served pursuant to Articles 12.3.1 and 12.3.2 shall provide, amongst other things, precise details of the Change in Law and its estimated impact on the TSP.

## Payment on account of Change in Law

### The payment for Change in Law shall be through a separate Bill. However, in case of any change in Monthly Transmission Charges by reason of Change in Law, as determined in accordance with this Agreement, the Bills to be raised by the Nodal Agency after such change in Transmission Charges shall appropriately reflect the changed Monthly Transmission Charges.

ARTICLE: 13

# Events of Default and Termination

## TSP’s Event of Default

The occurrence and continuation of any of the following events shall constitute a TSP Event of Default, unless any such TSP Event of Default occurs as a result of any non-fulfilment of its obligations as prescribed under this Agreement by the Nodal Agency or a Force Majeure Event:

- After having taken up the construction of the Project, the abandonment by the TSP or the TSP's Contractors of the construction of the Project for a continuous period of two (2) months and such default is not rectified within thirty (30) days from the receipt of notice from the Nodal Agency in this regard;

- The failure to commission any Element of the Project by the date falling six (6) months after its Scheduled COD unless extended by Nodal Agency as per provisions of this Agreement;

- If the TSP:

    - assigns, mortgages or charges or purports to assign, mortgage or charge any of its assets or rights related to the Project in contravention of the provisions of this Agreement; or

    - transfers or novates any of its obligations pursuant to this Agreement, in a manner contrary to the provisions of this Agreement;

Except where such transfer is in pursuance of a Law and

      - it does not affect the ability of the transferee to perform, and such transferee has the financial and technical capability to perform, its obligations under this Agreement;

      - is to a transferee who assumes such obligations under the Project and this Agreement remains effective with respect to the transferee;

- If:

    - The TSP becomes voluntarily or involuntarily the subject of any bankruptcy or insolvency or winding up proceedings and such proceedings remain uncontested for a period of thirty (30) days; or

    - any winding up or bankruptcy or insolvency order is passed against the TSP; or

    - the TSP goes into liquidation or dissolution or a receiver or any similar officer is appointed over all or substantially all of its assets or official liquidator is appointed to manage its affairs, pursuant to Law,

Provided that a dissolution or liquidation of the TSP will not be a TSP’s Event of Default, where such dissolution or liquidation of the TSP is for the purpose of a merger, consolidation or reorganization with the prior approval of the Commission as per the provisions of Central Electricity Regulatory Commission (Procedure, terms and Conditions for grant of Transmission License and other related matters) Regulations, 2006 or as amended from time to time; or

- Failure on the part of the TSP to comply with the provisions of Article 19.1 of this Agreement; or

- the TSP repudiates this Agreement and does not rectify such breach even within a period of thirty (30) days from a notice from the Nodal Agency in this regard; or

- after Commercial Operation Date of the Project, the TSP fails to achieve monthly Target Availability of 98%, for a period of six (6) consecutive months or within a non-consecutive period of  six (6) months within any continuous aggregate period of eighteen(18) months except where the Availability is affected by Force Majeure Events as per Article 11; or

- any of the representations and warranties made by the TSP in Article 17 of this Agreement being found to be untrue or inaccurate. Further, in addition to the above, any of the undertakings submitted by the Selected Bidder at the time of submission of the Bid being found to be breached or inaccurate, including but not limited to undertakings from its Parent Company / Affiliates related to the minimum equity obligation; or

- the TSP fails to complete / fulfil all the activities / conditions within the specified period as per Article 3; or

- except for the reasons solely attributable to Nodal Agency, the TSP is in material breach of any of its obligations under this Agreement and such material breach is not rectified by the TSP within thirty (30) days of receipt of notice in this regard from the Nodal Agency; or

- the TSP fails to take the possession of the land required for location specific substations, switching stations or HVDC terminal or inverter stations and / or fails to pay the requisite price to the parties and / or any State Government authority from whom the land is acquired, within twelve (12) months from the Effective Date.

## Termination Procedure for TSP Event of Default

- Upon the occurrence and continuance of any TSP’s Event of Default under Article 13.1 the Nodal Agency may serve notice on the TSP, with a copy to the CEA and the Lenders’ Representative, of their intention to terminate this Agreement (a "Nodal Agency’s Preliminary Termination Notice"), which shall specify in reasonable detail, the circumstances giving rise to such Nodal Agency’s Preliminary Termination Notice.

- Following the issue of a Nodal Agency’s Preliminary Termination Notice, the Consultation Period shall apply and would be for the Parties to discuss as to what steps shall be taken with a view to mitigate the consequences of the relevant Event of Default having regard to all the circumstances.

- During the Consultation Period, the Parties shall, save as otherwise provided in this Agreement, continue to perform their respective obligations/ roles under this Agreement, and the TSP shall not remove any material, equipment or any part of the Project, without prior consent of the Nodal Agency.

Following the expiry of the Consultation Period, unless the Parties shall have otherwise agreed to the contrary or the circumstances giving rise to Nodal Agency’s Preliminary Termination Notice shall have ceased to exist or shall have been remedied, this Agreement may be terminated by the Nodal Agency by giving a Termination Notice to the TSP, in writing, of at least seven (7) days, with a copy to CEA and the Lenders’ Representative in order to enable the Lenders to exercise right of substitution in accordance with Article 15.3 of this Agreement.

Further, the Nodal Agency may also initiate proceedings to blacklist the TSP & its Affiliates from participation in any RFP issued by BPCs for a period of 5 years.

## Procedure for Nodal Agency’s non-fulfilment of Role

- Upon the Nodal Agency not being able to fulfil its role under Article 4.2, the TSP may serve notice on the Nodal Agency, with a copy to CEA and the Lenders’ Representative (a "TSP’s Preliminary Notice"), which notice shall specify in reasonable detail the circumstances giving rise to such non-fulfilment of role by the Nodal Agency.

- Following the issue of a TSP’s Preliminary Notice, the Consultation Period shall apply.

- The Consultation Period would be for the Parties to discuss as to what steps shall be taken with a view to mitigate the consequences of the relevant non-fulfilment of role by the Nodal Agency including giving time extension to TSP, having regard to all the circumstances.

- During the Consultation Period, both Parties shall, save as otherwise provided in this Agreement, continue to perform their respective obligations/ roles under this Agreement.

## Termination due to Force Majeure

### In case the Parties could not reach an agreement pursuant to Articles 3.3.4 and 4.4.2 of this Agreement and the Force Majeure Event or its effects continue to be present, the Nodal Agency shall have the right to cause termination of the Agreement. In case of such termination, the Contract Performance Guarantee shall be returned to the TSP as per the provisions of Article 6.5.1.

### In case of termination of this Agreement, the TSP shall provide to the Nodal Agency the full names and addresses of its Contractors as well as complete designs, design drawings, manufacturing drawings, material specifications and technical information, as required by the Nodal Agency within thirty (30) days of Termination Notice.

## Termination or amendment due to non-requirement of any Element or Project during construction

### In case any Element or Project, which is under construction, is no longer required due to any reason whatsoever, the Nodal Agency may issue a notice to this effect to the TSP.

### Nodal agency may also issue notice to the TSP seeking their response to the proposed termination/ amendment (as the case may be) of the Agreement. The Nodal Agency shall issue copy of such notice to Lenders. In the notice, Nodal Agency shall also include an assessment of the physical progress made by TSP in the Element/ Project (as the case may be) that is no longer required.

### The TSP shall neither carry out further investment nor carry out any work on the Element/ Project (as the case may be) that is no longer required after delivery of the notice.

### After taking into account the comments of the TSP, the Nodal Agency may terminate the Agreement or amend it if both Parties agree to the amendment.

## Revocation of the Transmission License

### The Commission may, as per the provisions of the Electricity Act, 2003, revoke the Transmission License of the ISTS Licensee. Further, in such a case, the Agreement shall be deemed to have been terminated.

## Termination Payment

### If Agreement is terminated on account of Force Majeure Events, non-requirement of any Element or Project during Construction, Nodal Agency’s non-fulfilment of Role & TSP’s Event of Default, the TSP shall be entitled for Termination Payment equivalent to valuation of Project Assets. Upon payment, the Nodal Agency shall take over the Project Assets.

ARTICLE: 14

# Liability and Indemnification

## Indemnity

### The TSP shall indemnify, defend and hold the Nodal Agency harmless against:

### any and all third party claims, actions, suits or proceedings against the Nodal Agency for any loss of or damage to property of such third party, or death or injury to such third party, arising out of a breach by the TSP of any of its obligations under this Agreement, except to the extent that any such claim, action, suit or proceeding has arisen due to a negligent act or omission, breach of this Agreement or non-fulfilment of statutory duty on the part of Nodal Agency; and

### any and all losses, damages, costs and expenses including legal costs, fines, penalties and interest actually suffered or incurred by the Nodal Agency from third party claims arising by reason of:

### a breach by the TSP of any of its obligations under this Agreement, (provided that this Article 14 shall not apply to such breaches by the TSP, for which specific remedies have been provided for under this Agreement) except to the extent that any such losses, damages, costs and expenses including legal costs, fines, penalties and interest (together to constitute “Indemnifiable Losses”) has arisen due to a negligent act or omission, breach of this Agreement or non-fulfilment of statutory duty on the part of the Nodal Agency, or

### any of the representations and warranties of the TSP under this Agreement being found to be inaccurate or untrue.

### The Nodal Agency shall, in accordance with the Regulations framed by CERC in this regard, indemnify, defend and hold the TSP harmless against:

### any and all third party claims, actions, suits or proceedings against the TSP, for any loss of or damage to property of such third party, or death or injury to such third party, arising out of any material breach by the Nodal Agency of any of their roles under this Agreement, except to the extent that any such claim, action, suit or proceeding has arisen due to a negligent act or omission, breach of this Agreement or breach of statutory duty on the part of the TSP, its Contractors, servants or agents; and

### any and all losses, damages, costs and expenses including legal costs, fines, penalties and interest (‘Indemnifiable Losses’) actually suffered or incurred by the TSP from third party claims arising by reason of:

### any material breach by the Nodal Agency of any of its roles under this Agreement (provided that, this Article 14 shall not apply to such breaches by the Nodal Agency, for which specific remedies have been provided for under this Agreement), except to the extent that any such Indemnifiable Losses have arisen due to a negligent act or omission, breach of this Agreement or breach of statutory duty on the part of the TSP, its Contractors, servants or agents or

### any of the representations and warranties of the Nodal Agency under this Agreement being found to be inaccurate or untrue.

## Patent Indemnity:

### The TSP shall, subject to the Nodal Agency’s compliance with Article 14.2.1 (b), indemnify and hold harmless the Nodal Agency and its employees and officers from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, which the Nodal Agency may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright or other intellectual property right registered or otherwise existing at the date of the Agreement by reason of  the setting up of the Project by the TSP.

### Such indemnity shall not cover any use of the Project or any part thereof other than for the purpose indicated by or to be reasonably inferred from the Agreement, any infringement resulting from the misuse of the Project or any part thereof, or any products produced in association or combination with any other equipment, plant or materials not supplied by the TSP, pursuant to the Agreement.

### If any proceedings are brought or any claim is made against the Nodal Agency arising out of the matters referred to in Article 14.2.1(a), the Nodal Agency shall promptly give the TSP a notice thereof, and the TSP shall at its own expense take necessary steps and attend such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. The TSP shall promptly notify the Nodal Agency of all actions taken in such proceedings or claims.

### If the TSP fails to notify the Nodal Agency   within twenty-eight (28) days after receipt of such notice from the Nodal Agency under Article 14.2.1(b) above, that it intends to attend any such proceedings or claim, then the Nodal Agency  shall be free to attend the same on their own behalf at the cost of the TSP. Unless the TSP has so failed to notify the Nodal Agency within the twenty eight (28) days period, the Nodal Agency  shall make no admission that may be prejudicial to the defence of any such proceedings or claims.

### The Nodal Agency shall, at the TSP’s request, afford all available assistance to the TSP in attending to such proceedings or claim, and shall be reimbursed by the TSP for all reasonable expenses incurred in so doing.

### The Nodal Agency, in accordance with the Regulations framed by CERC in this regard, subject to the TSP’s compliance with Article 14.2.2(b) shall indemnify and hold harmless the TSP and its employees, officers from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs and expenses of whatsoever nature, including attorney’s fees and expenses, which the TSP may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright or other intellectual property right registered or otherwise existing at the date of the Agreement by reason of  the setting up of the Project by the TSP.

### If any proceedings are brought or any claim is made against the TSP arising out of the matters referred to in Article 14.2.2 (a) the TSP shall promptly give the Nodal Agency a notice thereof, and the Nodal Agency   shall at its own expense take necessary steps and attend such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. The Nodal Agency shall promptly notify the TSP of all actions taken in such proceedings or claims.

### If the Nodal Agency fails to notify the TSP within twenty-eight (28) days after receipt of such notice from the TSP under Article 14.2.2(b) above, that it intends to attend any such proceedings or claim, then the TSP shall be free to attend the same on its own behalf at the cost of the Nodal Agency. Unless the Nodal Agency has so failed to notify the TSP within the twenty (28) days period, the TSP shall make no admission that may be prejudicial to the defence of any such proceedings or claim.

### The TSP shall, at the Nodal Agency request, afford all available assistance to the Nodal Agency in attending to such proceedings or claim, and shall be reimbursed by the Nodal Agency for all reasonable expenses incurred in so doing.

## Monetary Limitation of liability

### A Party ("Indemnifying Party") shall be liable to indemnify the other Party ("Indemnified Party") under this Article 14 for any indemnity claims made in a Contract Year only up to an amount of Rupees Three Crore Eighty-Four Lakh Only (Rs. 3.84 Crore).

## Procedure for claiming indemnity

### Where the Indemnified Party is entitled to indemnification from the Indemnifying Party pursuant to Articles 14.1 or 14.2 the Indemnified Party shall promptly notify the Indemnifying Party of such claim, proceeding, action or suit referred to in Articles 14.1 or 14.2 in respect of which it is entitled to be indemnified. Such notice shall be given as soon as reasonably practicable after the Indemnified Party becomes aware of such claim, proceeding, action or suit. The Indemnifying Party shall be liable to settle the indemnification claim within thirty (30) days of receipt of the above notice.

### Provided however that, if:

### the Parties choose to contest, defend or litigate such claim, action, suit or proceedings in accordance with Article 14.4.3 below; and

### the claim amount is not required to be paid/deposited to such third party pending the resolution of the Dispute,

### the Indemnifying Party shall become liable to pay the claim amount to the Indemnified Party or to the third party, as the case may be, promptly following the resolution of the Dispute, if such Dispute is not settled in favour of the Indemnified Party.

### The Indemnified Party may contest, defend and litigate a claim, action, suit or proceeding for which it is entitled to be indemnified under Articles 14.1 or 14.2 and the Indemnifying Party shall reimburse to the Indemnified Party all reasonable costs and expenses incurred by the Indemnified Party. However, such Indemnified Party shall not settle or compromise such claim, action, suit or proceedings without first getting the consent of the Indemnifying Party, which consent shall not be unreasonably withheld or delayed.

### An Indemnifying Party may, at its own expense, assume control of the defence of any proceedings brought against the Indemnified Party if it acknowledges its obligation to indemnify such Indemnified Party, gives such Indemnified Party prompt notice of its intention to assume control of the defence, and employs an independent legal counsel at its own cost that is reasonably satisfactory to the Indemnified Party.

## Limitation on Liability

### Except as expressly provided in this Agreement, neither the TSP nor the Nodal Agency nor their respective officers, directors, agents, employees or Affiliates (including, officers, directors, agents or employees of such Affiliates), shall be liable or responsible to the other Party or its Affiliates including its officers, directors, agents, employees, successors, insurers or permitted assigns for incidental, indirect or consequential, punitive or exemplary damages, connected with or resulting from performance or non-performance of this Agreement, or anything done in connection herewith, including claims in the nature of lost revenues, income or profits (other than payments expressly required and properly due under this Agreement), any increased expense of, reduction in or loss of transmission capacity or equipment used therefore, irrespective of whether such claims are based upon breach of warranty, tort (including negligence, whether of the  Nodal Agency, the TSP or others), strict liability, contract, breach of statutory duty, operation of law or otherwise.

### The Nodal Agency shall have no recourse against any officer, director or shareholder of the TSP or any Affiliate of the TSP or any of its officers, directors or shareholders for such claims excluded under this Article. The TSP shall also have no recourse against any officer, director or shareholder of the Nodal Agency, or any Affiliate of the Nodal Agency or any of its officers, directors or shareholders for such claims excluded under this Article.

## Duty to Mitigate

The party entitled to the benefit of an indemnity under this Article 14 shall take all reasonable measures to mitigate any loss or damage which has occurred. If the Party fails to take such measures, the other Party’s liabilities shall be correspondingly reduced.

ARTICLE: 15

# Assignments and Charges

## Assignments:

### This Agreement shall be binding upon, and inure to the benefit of the Parties and their respective successors and permitted assigns. This Agreement shall not be assigned by any Party, except as provided in Article 15.3.

## Permitted Charges:

### Neither Party shall create or permit to subsist any encumbrance over all or any of its rights and benefits under this Agreement.

### However, the TSP may create any encumbrance over all or part of the receivables, or the Project Assets of the Project in favour of the Lenders or the Lenders’ Representative on their behalf, as security for amounts payable under the Financing Agreements and any other amounts agreed by the Parties.

### Provided that:

- the Lenders or the Lenders’ Representative on their behalf shall have entered into the Financing Agreements and agreed in writing to the provisions of this Agreement; and

- any encumbrance granted by the TSP in accordance with this Article 15.2.2 shall contain provisions pursuant to which the Lenders or the Lender’s Representative on their behalf agrees unconditionally with the TSP to release from such encumbrances upon payment by the TSP to the Lenders of all amounts due under the Financing Agreements.

### Article 15.2.1 does not apply to:

- liens arising by operation of law (or by an agreement evidencing the same) in the ordinary course of the TSP developing and operating the Project;

- pledges of goods, the related documents of title and / or other related documents, arising or created in the ordinary course of the TSP developing and operating the Project; or

- security arising out of retention of title provisions in relation to goods acquired in the ordinary course of the TSP developing and operating the Project.

## Substitution Rights of the Lenders

### The TSP would need to operate and maintain the Project under the provisions of this Agreement and cannot assign the Transmission License or transfer the Project or part thereof to any person by sale, lease, exchange or otherwise, without the prior approval of the Nodal Agency.

### However, in the case of default by the TSP in debt repayments or in the case of default by the TSP as per Article 13 of this Agreement during the debt repayments, the Commission may, on an application from the Lenders, assign the Transmission License to the nominee of the Lenders subject to the fulfilment of the qualification requirements and provisions of the Central Electricity Regulatory Commission (Procedure, terms and Conditions for grant of Transmission License and other related matters) Regulations, 2006 and as amended from time to time.

ARTICLE: 16

# Governing Law and Dispute Resolution

## Governing Law:

This Agreement shall be governed by and construed in accordance with the Laws of India. Any legal proceedings in respect of any matters, claims or disputes under this Agreement shall be under the jurisdiction of appropriate courts in Delhi.

## Amicable Settlement:

### Either Party is entitled to raise any claim, dispute or difference of whatever nature arising under, out of or in connection with this Agreement, including its existence or validity or termination or whether during the execution of the Project or after its completion and whether prior to or after the abandonment of the Project or termination or breach of the Agreement by giving a written notice to the other Party, which shall contain:

- a description of the Dispute;

- the grounds for such Dispute; and

- all written material in support of its claim.

### The other Party shall, within thirty (30) days of issue of notice issued under Article 16.2.1, furnish:

- counter-claim and defences, if any, regarding the Dispute; and

- all written material in support of its defences and counter-claim.

### Within thirty (30) days of issue of notice by the Party pursuant to Article 16.2.1, if the other Party does not furnish any counter claim or defense under Article 16.2.2, or thirty (30) days from the date of furnishing counter claims or defence by the other Party, both the Parties to the Dispute shall meet to settle such Dispute amicably.  If the Parties fail to resolve the Dispute amicably within thirty (30) days from the later of the dates mentioned in this Article 16.2.3, the Dispute shall be referred for dispute resolution in accordance with Article 16.3.

## Dispute Resolution:

### All Disputes shall be adjudicated by the Commission.

## Parties to Perform Obligations:

Notwithstanding the existence of any Dispute and difference referred to the Commission as provided in Article 16.3 and save as the Commission may otherwise direct by a final or interim order, the Parties hereto shall continue to perform their respective obligations/ roles (which are not in dispute) under this Agreement.

ARTICLE: 17

# Representation and Warranties

## Representation and warranties of the Nodal Agency

### The Nodal Agency hereby represents and warrants to and agrees with the TSP as follows and acknowledges and confirms that the TSP is relying on such representations and warranties in connection with the transactions described in this Agreement:

- It has all requisite powers and authority to execute and consummate this Agreement;

- This Agreement is enforceable against the Nodal Agency in accordance with its terms;

- The consummation of the transactions contemplated by this Agreement on the part of Nodal Agency will not violate any provision of nor constitute a default under, nor give rise to a power to cancel any charter, mortgage, deed of trust or lien, lease, agreement, license, permit, evidence of indebtedness, restriction, or other contract to which the Nodal Agency is a Party or to which the Nodal Agency is bound, which violation, default or power has not been waived;

## Representation and Warranties of the TSP:

### The TSP hereby represents and warrants to and agrees with the Nodal Agency as follows and acknowledges and confirms that the Nodal Agency is relying on such representations and warranties in connection with the transactions described in this Agreement:

- It has all requisite powers and has been duly authorized to execute and consummate this Agreement;

- This Agreement is enforceable against it, in accordance with its terms;

- The consummation of the transactions contemplated by this Agreement on the part of the TSP will not violate any provision of nor constitute a default under, nor give rise to a power to cancel any charter, mortgage, deed of trust or lien, lease, agreement, license, permit, evidence of indebtedness, restriction, or other contract to which the TSP is a Party or to which the TSP is bound which violation, default or power has not been waived;

- The TSP is not insolvent and no insolvency proceedings have been instituted, nor threatened or pending by or against the TSP;

- There are no actions, suits, claims, proceedings or investigations pending or, to the best of the TSP’s  knowledge, threatened in writing against the TSP at law, in equity, or otherwise, and whether civil or criminal in nature, before or by, any court, commission, arbitrator or governmental agency or authority, and there are no outstanding judgments, decrees or orders of any such courts, commission, arbitrator or governmental agencies or authorities, which materially adversely affect its ability to execute the Project or to comply with its obligations under this Agreement.

### The TSP makes all the representations and warranties above to be valid as on the Effective Date of this Agreement.

ARTICLE: 18

# Independent Engineer

18.1	Appointment of Independent Engineer

The Nodal Agency shall appoint an agency/ company as Independent Engineer as per framework provided in the Guidelines for Encouraging Competition in Development of Transmission Projects for selection of Independent Engineer.

18.2	Roles and functions of Independent Engineer

The role and functions of the Independent Engineer shall include the following:

  - Progress Monitoring as required under this Agreement;

  - Ensuring Quality as required under this Agreement;

  - determining, as required under the Agreement, the costs of any works or services and/or their reasonableness during construction phase;

  - determining, as required under the Agreement, the period or any extension thereof, for performing any duty or obligation during construction phase;

  - determining, as required under the Agreement, the valuation of the Project Assets.

  - Assisting the Parties in resolution of Disputes and

  - Undertaking all other duties and functions in accordance with the Agreement.

18.3	Remuneration of Independent Engineer

The fee and charges of the Independent Engineer shall be paid by the Nodal Agency as per terms & conditions of appointment.

18.4	Termination of appointment

18.4.1	The Nodal Agency may, in its discretion, terminate the appointment of the Independent Engineer at any time, but only after appointment of another Independent Engineer.

18.4.2	If the TSP has reason to believe that the Independent Engineer is not discharging its duties and functions in a fair, efficient and diligent manner, it may make a written representation to the Nodal Agency and seek termination of the appointment of the Independent Engineer. Upon receipt of such representation, the Nodal Agency shall hold a tripartite meeting with the TSP and Independent Engineer for an amicable resolution, and the decision of Nodal agency is final. In the event that the appointment of the Independent Engineer is terminated hereunder, the Nodal Agency shall appoint forthwith another Independent Engineer.

18.5	Authorised signatories

The Nodal Agency shall require the Independent Engineer to designate and notify to the Nodal Agency up to 2 (two) persons employed in its firm to sign for and on behalf of the Independent Engineer, and any communication or document required to be signed by the Independent Engineer shall be valid and effective only if signed by any of the designated persons; provided that the Independent Engineer may, by notice in writing, substitute any of the designated persons by any of its employees.

ARTICLE: 19

# Miscellaneous Provisions

## Equity Lock-in Commitment:

### The aggregate equity share holding of the Selected Bidder in the issued and paid up equity share capital of Beawar Transmission Limited shall not be less than Fifty-one percent (51%) up to a period of one (1) year after COD of the Project.

### Provided that, in case the Lead Member or Bidding Company is holding equity through Affiliate/s, Ultimate Parent Company or Parent Company, such restriction as specified above shall apply to such entities.

### Provided further, that in case the Selected Bidder is a Bidding Consortium, the Lead Member shall continue to hold equity of at least twenty-six percent (26%) upto a period of one (1) year after COD of the Project and any Member of such Bidding Consortium shall be allowed to divest its equity as long as the other remaining Members (which shall always include the Lead Member) hold the minimum equity specified above.

### If equity is held by the Affiliates, Parent Company or Ultimate Parent Company of the Selected Bidder, then, subject to the second proviso to Article 19.1.1, such Affiliate, Parent Company or Ultimate Parent Company shall be eligible to transfer its shareholding in Beawar Transmission Limited to another Affiliate or to the Parent Company / Ultimate Parent Company of the Selected Bidder. If any such shareholding entity, qualifying as an Affiliate / Parent Company / Ultimate Parent Company, is likely to cease to meet the criteria to qualify as an Affiliate / Parent Company / Ultimate Parent Company, the shares held by such entity shall be transferred to another Affiliate / Parent Company / Ultimate Parent Company of the Selected Bidder.

### Subject to Article 19.1.1, all transfer(s) of shareholding of Beawar Transmission Limited by any of the entities referred to in Article 19.1.1 and 19.1.2 above, shall be after prior written intimation to the Nodal Agency.

### For computation of effective Equity holding, the Equity holding of the Selected Bidder or its Ultimate Parent Company in such Affiliate(s) or Parent Company and the equity holding of such Affiliate(s) or Ultimate Parent Company in Beawar Transmission Limited shall be computed in accordance with the example given below:

### If the Parent Company or the Ultimate Parent Company of the Selected Bidder A directly holds thirty percent (30%) of the equity in Beawar Transmission Limited, then holding of Selected Bidder A in Beawar Transmission Limited shall be thirty percent (30%);

### If Selected Bidder A holds thirty percent (30%) equity of the Affiliate and the Affiliate holds fifty percent (50%) equity in Beawar Transmission Limited, then, for the purposes of ascertaining the minimum equity/equity lock-in requirements specified above, the effective holding of Bidder A in Beawar Transmission Limited shall be fifteen percent (15%), (i.e., 30% x 50%)

### The provisions as contained in this Article 19.1 shall override the terms of the consortium agreement submitted as part of the Bid.

### The TSP shall be responsible to report to Nodal Agency, within thirty (30) days from the occurrence of any event that would result in any change in its equity holding structure from that which existed as on the date of signing of the Share Purchase Agreement. In such cases, the Nodal Agency would reserve the right to ascertain the equity holding structure and to call for all such required documents / information / clarifications as may be required.

## Commitment of maintaining Qualification Requirement

### The Selected Bidder will be required to continue to maintain compliance with the Qualification Requirements, as stipulated in RFP Document, till the COD of the Project. Where the Technically Evaluated Entity and/or the Financially Evaluated Entity is not the Bidding Company or a Member in a Bidding Consortium, as the case may be, the Bidding Company or Member shall continue to be an Affiliate of the Technically Evaluated Entity and/or Financially Evaluated Entity till the COD of the Project.

### Failure to comply with the aforesaid provisions shall be dealt in the same manner as TSP’s Event of Default as under Article 13 of this Agreement.

## Language:

### All agreements, correspondence and communications between the Parties relating to this Agreement and all other documentation to be prepared and supplied under the Agreement shall be written in English, and the Agreement shall be construed and interpreted in accordance with English language.

### If any of the agreements, correspondence, communications or documents are prepared in any language other than English, the English translation of such agreements, correspondence, communications or documents shall prevail in matters of interpretation.

## Affirmation

The TSP and the Nodal Agency, each affirm that:

- neither it nor its respective directors, employees, or agents has paid or undertaken to pay or shall in the future pay any unlawful commission, bribe, pay-off or kick-back; and

- it has not in any other manner paid any sums, whether in Indian currency or foreign currency and whether in India or abroad to the other Party to procure this Agreement, and the TSP and the Nodal Agency hereby undertake not to engage in any similar acts during the Term of Agreement.

## Severability

The invalidity or enforceability, for any reason, of any part of this Agreement shall not prejudice or affect the validity or enforceability of the remainder of this Agreement, unless the part held invalid or unenforceable is fundamental to this Agreement.

## Counterparts

This Agreement may be executed in one or more counterparts, each of which shall be deemed an original and all of which collectively shall be deemed one and the same Agreement.

## Breach of Obligations/ Roles

The Parties acknowledge that a breach of any of the obligations/ roles contained herein would result in injuries. The Parties further acknowledge that the amount of the liquidated damages or the method of calculating the liquidated damages specified in this Agreement is a genuine and reasonable pre-estimate of the damages that may be suffered by the non-defaulting Party in each case specified under this Agreement.

## Restriction of Shareholders / Owners Liability

### Parties expressly agree and acknowledge that none of the shareholders of the Parties hereto shall be liable to the other Parties for any of the contractual obligations of the concerned Party under this Agreement.

### Further, the financial liabilities of the shareholder(s) of each Party to this Agreement shall be restricted to the extent provided in the Indian Companies Act, 1956 / Companies Act, 2013 (as the case may be).

## Taxes and Duties:

### The TSP shall bear and promptly pay all statutory taxes, duties, levies and cess, assessed/levied on the TSP, its Contractors or their employees that are required to be paid by the TSP as per the Law in relation to the execution of the Project and for providing Transmission Service as per the terms of this Agreement.

### The Nodal Agency shall be indemnified and held harmless by the TSP against any claims that may be made against the Nodal Agency in relation to the matters set out in Article 19.9.1.

### The Nodal Agency shall not be liable for any payment of, taxes, duties, levies, cess whatsoever for discharging any obligation of the TSP by the Nodal Agency on behalf of TSP or its personnel, provided the TSP has consented in writing to the Nodal Agency for such work, for which consent shall not be unreasonably withheld.

## No Consequential or Indirect Losses

The liability of the TSP shall be limited to that explicitly provided in this Agreement.

Provided that, notwithstanding anything contained in this Agreement, under no event shall the Nodal Agency or the TSP claim from one another any indirect or consequential losses or damages.

## Discretion:

Except where this Agreement expressly requires a Party to act fairly or reasonably, a Party may exercise any discretion given to it under this Agreement in any way it deems fit.

## Confidentiality

### The Parties undertake to hold in confidence this Agreement and RFP Project Documents and not to disclose the terms and conditions of the transaction contemplated hereby to third parties, except:

### to their professional advisors;

### to their officers, contractors, employees, agents or representatives, financiers, who need to have access to such information for the proper performance of their activities; or

### disclosures required under Law,

without the prior written consent of the other Parties.

Provided that, the TSP agrees and acknowledges that the Nodal Agency, may, at any time, disclose the terms and conditions of the Agreement and the RFP Project Documents to any person, to the extent stipulated under the Law and the Competitive Bidding Guidelines.

## Order of priority in application:

Save as provided in Article 2.5, in case of inconsistencies between the terms and conditions stipulated in Transmission License issued by the Commission to the TSP, agreement(s) executed between the Parties, applicable Law including rules and regulations framed thereunder, the order of priority as between them shall be the order in which they are placed below:

- terms and conditions of Transmission License;

- applicable Law, rules and regulations framed thereunder;

- this Agreement;

- Agreement(s), if any, under Sharing Regulations.

## Independent Entity:

### The TSP shall be an independent entity performing its obligations pursuant to the Agreement.

### Subject to the provisions of the Agreement, the TSP shall be solely responsible for the manner in which its obligations under this Agreement are to be performed. All employees and representatives of the TSP or Contractors engaged by the TSP in connection with the performance of the Agreement shall be under the complete control of the TSP and shall not be deemed to be employees, representatives, Contractors of the Nodal Agency and nothing contained in the Agreement or in any agreement or contract awarded by the TSP shall be construed to create any contractual relationship between any such employees, representatives or Contractors and the Nodal Agency.

## Amendments:

### This Agreement may only be amended or supplemented by a written agreement between the Parties.

## Waiver:

### No waiver by either Party of any default or breach by the other Party in the performance of any of the provisions of this Agreement shall be effective unless in writing duly executed by an authorised representative of such Party.

### Neither the failure by either Party to insist on any occasion upon the performance of the terms, conditions and provisions of this Agreement nor time or other indulgence granted by one Party to the other Parties shall act as a waiver of such breach or acceptance of any variation or the relinquishment of any such right or any other right under this Agreement, which shall remain in full force and effect.

## Relationship of the Parties:

### This Agreement shall not be interpreted or construed to create an association, joint venture, or partnership or agency or any such other relationship between the Parties or to impose any partnership obligation or liability upon either Party and neither Party shall have any right, power or authority to enter into any agreement or undertaking for, or act on behalf of, or to act as or be an agent or representative of, or to otherwise bind, the other Party.

## Entirety:

### This Agreement along with its sections, schedules and appendices is intended by the Parties as the final expression of their agreement and is intended also as a complete and exclusive statement of the terms of their agreement.

### Except as provided in this Agreement, all prior written or oral understandings, offers or other communications of every kind pertaining to this Agreement or the provision of Transmission Service under this Agreement to the Nodal Agency by the TSP shall stand superseded and abrogated.

## Notices:

### All notices or other communications which are required to be given under this Agreement shall be in writing and in the English language

### If to the TSP, all notices or communications must be delivered personally or by registered post or facsimile or any other mode duly acknowledged to the addressee below:

Address		:

Attention		:

Email			:

Fax. No.		:

Telephone No.	:

### If to the Nodal Agency, all notices or communications must be delivered personally or by registered post or facsimile or any other mode duly acknowledged to the addresses below:

(i)	CENTRAL TRANSMISSION UTILITY OF INDIA LIMITED

Address		:  Plot No.2, Sector – 29, Gurugram, Haryana-

122001, India

Attention                  :  Mr. Vikram Singh Bhal, ED

Email			:  vsbhal@powergrid.in

Fax. No.		:

Telephone No.	:  9910378068

### All notices or communications given by facsimile shall be confirmed by sending a copy of the same via post office in an envelope properly addressed to the appropriate Party for delivery by registered mail.  All notices shall be deemed validly delivered upon receipt evidenced by an acknowledgement of the recipient, unless the Party delivering the notice can prove in case of delivery through the registered post that the recipient refused to acknowledge the receipt of the notice despite efforts of the postal authorities.

### Any Party may by notice of at least fifteen (15) days to the other Party change the address and/or addresses to which such notices and communications to it are to be delivered or mailed.

## Fraudulent and Corrupt Practices

### The TSP and its respective officers, employees, agents and advisers shall observe the highest standard of ethics during the subsistence of this Agreement. Notwithstanding anything to the contrary contained in the Agreement, the Nodal Agency may terminate the Agreement without being liable in any manner whatsoever to the TSP, if it determines that the TSP has, directly or indirectly or through an agent, engaged in corrupt practice, fraudulent practice, coercive practice, undesirable practice or restrictive practice in the Bid process. In such an event, the Nodal Agency shall forfeit the Contract Performance Guarantee of the TSP, without prejudice to any other right or remedy that may be available to the Nodal Agency hereunder or subsistence otherwise.

### Without prejudice to the rights of the Nodal Agency under Clause 19.20.1 hereinabove and the rights and remedies which the Nodal Agency may have under this Agreement, if a TSP is found by the Nodal Agency to have directly or indirectly or through an agent, engaged or indulged in any corrupt practice, fraudulent practice, coercive practice, undesirable practice or restrictive practice during the Bid process, or after the issue of Letter of Intent (hereinafter referred to as LoI) or after the execution of the agreement(s) required under Sharing Regulations, the Nodal Agency may terminate the Agreement without being liable in any manner whatsoever to the TSP. Further, the TSP & its Affiliates shall not be eligible to participate in any tender or RFP issued by any BPC for an indefinite period from the date such TSP is found by the Nodal Agency to have directly or indirectly or through an agent, engaged or indulged in any corrupt practice, fraudulent practice, coercive practice, undesirable practice or restrictive practices, as the case may be.

### For the purposes of this Clause 19.20, the following terms shall have the meaning hereinafter respectively assigned to them:

(a) “corrupt practice” means (i) the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence the actions of any person connected with the Bid process (for avoidance of doubt, offering of employment to or employing or engaging in any manner whatsoever, directly or indirectly, any official of the BPC who is or has been associated or dealt in any manner, directly or indirectly with the Bid process or the LoI or has dealt with matters concerning the RFP Project Documents or arising there from, before or after the execution thereof, at any time prior to the expiry of one year from the date such official resigns or retires from or otherwise ceases to be in the service of the BPC, shall be deemed to constitute influencing the actions of a person connected with the Bid Process); or (ii) engaging in any manner whatsoever, whether during the Bid Process or after the issue of the LoI or after the execution of the RFP Project Documents, as the case may be, any person in respect of any matter relating to the Project or the LoI or the RFP Project Documents, who at any time has been or is a legal, financial or technical adviser of the BPC in relation to any matter concerning the Project;

(b)“fraudulent practice” means a misrepresentation or omission of facts or suppression of facts or disclosure of incomplete facts, in order to influence the Bid process;

(c) “coercive practice” means impairing or harming, or threatening to impair or harm, directly or indirectly, any person or property to influence any person’s participation or action in the Bid process;

(d) “undesirable practice” means (i) establishing contact with any person connected with or employed or engaged by the BPC with the objective of canvassing, lobbying or in any manner influencing or attempting to influence the Bid process; or (ii) having a Conflict of Interest; and

(e) “restrictive practice” means forming a cartel or arriving at any understanding or arrangement among Bidders with the objective of restricting or manipulating a full and fair competition in the Bid process;

## Compliance with Law:

### Despite anything contained in this Agreement but without prejudice to Article 12, if any provision of this Agreement shall be in deviation or inconsistent with or repugnant to the provisions contained in the Electricity Act, 2003, or any rules and regulations made there under, such provision shall be deemed to be amended to the extent required to bring it into compliance with the aforesaid relevant provisions as amended from time to time.

### IN WITNESS WHEREOF, THE PARTIES HAVE CAUSED THIS AGREEMENT TO BE EXECUTED BY THEIR DULY AUTHORISED REPRESENTATIVES AS OF THE DATE AND PLACE SET FORTH ABOVE.

1.	                    	For and on behalf of TSP

……………………………..

[Signature, Name, Designation and Address]

2.	For and on behalf of .........................[Insert name of the Nodal Agency]

……………………………..

[Signature, Name, Designation and Address]

WITNESSES:

1. 	For and on behalf of

: BPC

……………………………

[Signature]

### ...............................................................

### [Insert, Name, Designation and Address of the Witness]

2.	For and on behalf of

: Nodal Agency

……………………………

[Signature]

### ...........................................................

### [Insert Name, Designation and Address of the Witness]

SCHEDULES

Schedule: 1

Project Description and Scope of Project

| Sl. No. | Scope of the Transmission Scheme | Scheduled COD in months from Effective Date |
| --- | --- | --- |
| 1 | Establishment of 2x1500MVA 765/400kV Substation at suitable location near Beawar along with 2x330 MVAr 765kV Bus Reactor & 2x125 MVAr 420kV Bus Reactor 765/400kV 1500 MVA ICTs: 2 nos. (7x500 MVA, including one spare unit) 330 MVAr, 765 kV bus reactor- 2 nos. (7x110 MVAr, including one spare unit) 765kV ICT bays – 2 nos. 400 kV ICT bays – 2 nos. 765 kV line bays – 6 nos. 400kV line bay- 2 nos. 765kV reactor bay- 2 nos. 125 MVAr, 420kV bus reactor – 2 nos. 420 kV reactor bay – 2 nos. Future provisions: Space for 765/400kV ICTs along with bays: 2 nos. 765kV line bay along with switchable line reactor: 8 nos. 765kV Bus Reactor along with bays:2 nos. 400/220 kV ICTs along with bays: 2nos. 400 kV line bays along with switchable line reactor: 4 nos. 400kV Bus Reactor along with bays: 1no. 220 kV line bays: 4nos. | 18 |
| 2 | LILO of both circuit of Ajmer-Chittorgarh 765 kV D/c at Beawar |  |
| 3 | LILO of 400kV Kota –Merta line at Beawar |  |
| 4 | Fatehgarh-3– Beawar 765 kV D/c along with 330 MVAr Switchable line reactor for each circuit at each end of Fatehgarh-3– Beawar 765 kV D/c line Switching equipment for 765 kV 330 MVAR switchable line reactor –4 nos. 765 kV, 330 MVAr Switchable line reactor- 4 nos. |  |
| 5. | ± 2x300MVAr STATCOM, 4x125 MVAr MSC, 2x125 MVAr MSR at Fatehgarh- 3 PS along with 2 nos. of 400 kV bays at Fatehgarh-3 PS | 24 |

Note:

        - POWERGRID to provide space for 765kV switchable line reactors at Fatehgarh-3 S/s (for 765kV Fatehgarh-3 PS – Beawar D/c line) for which no cost is envisaged. Two (02) nos. 765 KV line bays at Fatehgarh-III PS for interconnection of Fatehgarh-3– Beawar 765 kV D/c line is under the scope of M/s POWERGRID.

        - ±300 MVAr STATCOM should be placed in each 400 kV bus section of Fatehgarh-3 PS (Phase-III Part E1).

        - POWERGRID shall provide space at Fatehgarh-3 S/s for STATCOM along with MSC & MSR and associated 400kV bays.

Project Description

In order to integrate and evacuate power from additional potential of renewable energy zones (20 GW) in Rajasthan (Fatehgarh: 9.1GW, Bhadla: 8GW, Ramgarh: 2.9GW) over and above 17 GW Solar Energy Zones (SEZ), various transmission alternatives were evolved & discussed with stakeholders and deliberated in the 3rd NRPC-TP meeting held on 19th February, 2021. Based on the discussions, hybrid (EHVAC & HVDC) transmission system was agreed in above meeting for evacuation of power from additional 20 GW REZ in Rajasthan (Phase-III).

As part of Phase-III system, Fatehgarh-4 & Bhadla-3 Pooling stations (new) are to be established which will be interconnected with Fatehgarh-3 & Fatehgarh-2 PS respectively. Further, renewable sources in Ramgarh complex are also proposed to be pooled at Ramgarh PS which shall be interconnected with Bhadla-3 PS. In view of integration & evacuation of additional 20 GW RE in Rajasthan with reliability as well as taking care of RE variability, under Phase-III System, Hybrid transmission system comprising EHV AC (765kV) & HVDC corridors are planned towards Delhi & Southern UP.

The subject transmission scheme involves establishment of 765/400kV Substation at suitable location near Beawar, implementation of Fatehgarh-3– Beawar 765 kV D/c line, LILO of both circuit of Ajmer-Chittorgarh 765 kV D/c at Beawar and LILO of 400kV Kota –Merta line at Beawar S/s which shall facilitate evacuation of RE power from Fatehgarh complex to Beawar and onward dispersal of power beyond Beawar to various beneficiaries.

Above transmission system for evacuation of power from REZ in Rajasthan (20 GW) under Phase III was also agreed in 49th Northern Region Power Committee (NRPC) meeting held on 27th September 2021 & 5th National Committee on Transmission (NCT) held on 25th August, 2021 and 2nd September, 2021. Further, Ministry of Power, Government of India, vide its Gazette Notification CG-DL-E-08122021-231686 (No. 4661) dated 06.12.2021 declared establishment of Ramgarh PS along with its interconnections through tariff based competitive bidding process route as part of “Transmission system for evacuation of power from REZ in Rajasthan (20 GW) under Phase III”.

Subsequently, due to many issues related to reactive power management in Western Rajasthan i.e. oscillations, abrupt voltage variations, low voltages in peak solar generation period & high voltage in off solar generation period, it was proposed to implement ± 2x300MVAr STATCOM, 4x125 MVAr MSC, 2x125 MVAr MSR at Ramgarh PS to support the grid. Above STATCOM was already approved as part of Phase-III scheme in 5th NCT meeting held on 25.08.2021 & 02.09.2021. Implementation of above STATCOM was agreed in 11th NCT meeting held on 28.12.2022 and 17.01.2023. During above meeting, it was also agreed that STACOM may be implemented as part of “Transmission system for evacuation of power from REZ in Rajasthan (20 GW) under Phase III Part-C1”. Implementation time of STATCOM was also agreed as 24 months in 12th NCT meeting held on 24.03.2023.

SPECIFIC TECHNICAL REQUIREMENTS FOR TRANSMISSION LINE

- The design, routing and construction of transmission lines shall be in accordance with Chapter V, Part A of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 2010, as amended from time to time.

A.2.0     Selection of tower type shall be made as per CEA Regulations, however in case lattice type towers are used, the following shall also be applicable:

A.2.1   Steel section of grade E 250 and/or grade E 350 as per IS 2062, only are permitted for use in towers, extensions, gantry structures and stub setting templates. For towers in snowbound areas, steel sections shall conform to Grade-C of IS-2062.

A.2.2     Towers shall be designed as per IS-802:2015, however the drag coefficient of the tower shall be as follows: -

| Solidity Ratio | Drag Coefficient |
| --- | --- |
| Upto 0.05 | 3.6 |
| 0.1 | 3.4 |
| 0.2 | 2.9 |
| 0.3 | 2.5 |
| 0.4 | 2.2 |
| 0.5 and above | 2.0 |

A.3.0	Transmission Service Provider (TSP) shall adopt any additional loading/design criteria for ensuring reliability of the line, if so desired and /or deemed necessary.

A.4.0    Transmission line shall be designed considering wind zones as specified in wind map given in National Building Code 2016, Vol.1. The developer shall also make his own assessment of local wind conditions and frequent occurrences of high intensity winds (HIW) due to thunderstorms, dust-storms, downburst etc. along the line route and wherever required, higher wind zone than that given in wind map shall be considered for tower design for ensuring reliability of line. Further, for transmission line sections passing within a distance of 50 km from the boundary of two wind zones, higher of the two wind zones shall be considered for design of towers located in such sections.

A.5.0   	765 kV towers, triple and quadruple circuit towers and towers with more than two sub-conductors per phase up to 400 kV shall be designed for reliability level 2. However, tall river crossing towers and special towers shall be designed for reliability level 3.

A.6.0    A) For power line crossing of 400 kV or above voltage level (if crossing over the existing line), large angle & dead end   towers (i.e. D/DD/QD) shall be used on either side of power line crossing.

B) For power line crossing of 132kV and 220kV (or 230kV) voltage level, angle towers(B/C/D/DB/DC/DD/QB/QC/QD) shall be used on either side of power line crossing depending upon the merit of the prevailing site condition and line deviation requirement.

C) For power line crossing of 66 kV and below voltage level, suspension/tension towers shall be provided on either side of power line crossing depending upon the merit of the prevailing site condition and line deviation requirement.

D) For crossing of railways, national highways and state highways, rules/regulations of appropriate authorities shall be followed.

A.7.0   The relevant conductor configuration shall be as follows: -

Type of conductor: ACSR / AAAC / AL59

Basic parameters:

| Transmission line | ACSR Conductor specified | Equivalent AAAC conductor based on 53.5% conductivity of Al Alloy | Equivalent AL59 conductor based on 59% conductivity of AL Alloy* | Sub-conductor Spacing |
| --- | --- | --- | --- | --- |
| 765kV D/C (Hexa Zebra) transmission lines | Zebra: Stranding 54/3.18 mm-Al + 7/3.18 mm-Steel, 428 sq mm, Aluminium area, 28.62 mm diameter Maximum DC Resistance at 20°C (Ω/km): 0.06868 Minimum UTS: 130.32 kN | Stranding details: 61/3.19mm, 28.71 mm diameter; 487.5 sq.mm Aluminium alloy area Maximum DC Resistance at 20°C (Ω/km): 0.06815 Minimum UTS: 135.6 kN | Stranding details: 61/3.08mm, 27.72 mm diameter; 454 sq.mm Aluminium alloy area Maximum DC Resistance at 20°C (Ω/km): 0.0653 Minimum UTS: 108 kN | 457 mm |
| 400kV D/C (Twin Moose) transmission lines | Moose: Stranding 54/3.53mm-Al + 7/3.53 mm-Steel, 31.77 mm diameter 528.5 sq. mm, Aluminium area, Maximum DC Resistance at 20°C (Ω/km): 0.05552 Minimum UTS: 161.20 kN | Stranding details: 61/3.55mm 31.95mm diameter; 604 sq. mm Aluminium alloy area Maximum DC Resistance at 20°C (Ω/km): 0.05506 Minimum UTS: 159.80 kN | Stranding details: 61/3.31 mm 29.79 mm diameter; 525 sq. mm Aluminium alloy area Maximum DC Resistance at 20°C (Ω/km): 0.0566 Minimum UTS: 124.70 kN | 450 mm |

Note:

1.  *To select any size above the minimum, the sizes mentioned in the Indian standard i.e IS-398(part-6) should be followed.

2.  The transmission lines shall have to be designed for a maximum operating conductor temperature of 85 deg C.

A.8.0	The required phase to phase spacing and horizontal spacing for 765kV and 400kV line shall be governed by the tower design as well as minimum live metal clearances for 765kV and 400kV voltage level under different insulator swing angles. However, the phase to phase spacing for 765kV and 400kV lines shall not be less than 15m and 8m respectively.

A.9.0	All electrical clearances including minimum live metal clearance, ground clearance and minimum mid span separation between earth wire and conductor shall be as per Central Electricity Authority (Measures Relating to Safety & Electric Supply) Regulations as amended from time to time and IS: 5613. Since these clearances for 765kV are not included in CEA Regulation/ Indian Standard, following values shall be considered:

Minimum live metal clearances for 765 kV line:

- (i) Under stationary conditions:

From tower body: 	For 765 kV D/C: 6.1 m

For 765 kV S/C: 5.6 m

(ii) Under Swing conditions

| Wind Pressure Condition | Minimum Electrical Clearance |
| --- | --- |
| a) Swing angle (25º) | 4.4 mtrs |
| b) Swing angle (55º) | - mtrs |

- Minimum ground clearance: 18 m

- Minimum mid span separation between earthwire and conductor: 9.0 m

Minimum live metal clearances for 400 kV line:

- (i)  Under stationary conditions:

From tower body: 3.05m

(ii)   Under Swing conditions

| Wind Pressure Condition | Minimum Electrical Clearance |
| --- | --- |
| a) Swing angle (22º) | 3.05 mtrs |
| b) Swing angle (44º) | - mtrs |

- Minimum ground clearance: 8.84 m

- Minimum mid span separation between earthwire and conductor: 9.0 m

A.10.0	Shielding angle shall not exceed 10 deg for 765kV D/C and 20 deg for 400kV transmission line.

A.11.0	The Fault current for design of line shall be 50kA for 1 sec for 765kV and 63kA for 1 sec for 400kV.

A.12.0	In case of 765kV & 400kV voltage class lines, at least one out of two earth wires shall be OPGW and second earth wire, if not OPGW, shall be either of galvanized standard steel (GSS) or AACSR or any other suitable conductor type depending upon span length and other technical consideration.

A.13.0	Each tower shall be earthed such that tower footing impedance does not exceed 10 ohms. Pipe type or Counterpoise type earthing shall be provided in accordance with relevant IS. Additional earthing shall be provided on every 7 to 8 kms distance at tension tower for direct earthing of both shield wires. If site condition demands, multiple earthing or use of earthing enhancement compound shall be used.

A14.0	Pile type foundation shall be used for towers located in river or creek bed or on bank of river having scourable strata or in areas where river flow or change in river course is anticipated, based on detailed soil investigation and previous years’ maximum flood discharge of the river, maximum velocity of water, highest flood level, scour depth & anticipated change in course of river based on river morphology data of at least past 20 years to ensure availability and reliability of the transmission line.

A.15.0	Transmission line route shall be finalized, in consultation with appropriate authorities so as to avoid the habitant zones of endangered species and other protected species. Bird diverters, wherever required, shall be provided on the line.

A.16.0	The raised chimney foundation is to be provided in areas prone to flooding/water stagnation like paddy field /agricultural field & undulated areas to avoid direct contact of water with steel part of tower. The top of the chimney of foundation should be at least above HFL (High Flood Level) or the historical water stagnation/ logging level (based on locally available data) or above High Tide Level or 500 mm above Natural Ground level (whichever is higher).

A.17.0 	Routing of transmission line through protected areas of India shall be avoided to the extent possible. In case, it is not possible to avoid protected areas, the towers of the transmission line upto 400 kV level which are installed in protected areas shall be designed for Multicircuit (4 circuits) configuration of same voltage level considering reliability level of at least two (2). The top two circuits of these multi-circuit towers shall be used for stringing of the transmission line under present scope and the bottom two circuits shall be made available for stringing of any future transmission line of any transmission service providers / State transmission utilities/Central transmission utilities passing through the same protected area. Further, the configuration and coordinates of such transmission towers shall be submitted to CEA, CTU & BPC by the TSP.

SPECIFIC TECHNICAL REQUIREMENTS FOR SUBSTATION

The proposed 765/400/220kV substation near Beawar shall be conventional AIS type generally conforming to the requirements of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 2010, as amended from time to time.

Extension of 765kV Fatehgarh-3 substation shall be conventional AIS type generally conforming to the requirements of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 2010, as amended from time to time.

B.1.0	Salient features of Substation Equipment and Facilities

The design and specification of substation equipment are to be governed by the following factors:

B.1.1	Insulation Coordination

The system design parameters for substations/switchyards shall be as given below:

| Sl No | Description of parameters | 765/400kV Beawar s/s |  | Extn. of 765kV Fatehgarh-3 s/s |
| --- | --- | --- | --- | --- |
|  |  | 765 kV System | 400 kV System | 765 kV System |
| 1. | System operating voltage | 765kV | 400kV | 765kV |
| 2. | Maximum voltage of the system (rms) | 800kV | 420kV | 800kV |
| 3. | Rated frequency | 50Hz | 50Hz | 50Hz |
| 4. | No. of phase | 3 | 3 | 3 |
| 5. | Rated Insulation levels |  |  |  |
| i) | Impulse withstand voltage for (1.2/50 micro sec.) - for equipment other than Transformer and Reactor - for Insulator String | 2100kVp 2100kVp | 1425kVp 1550kVp | 2100kVp 2100kVp |
| ii) | Switching impulse withstand voltage (250/2500 micro sec.) dry and wet | 1550kVp | 1050kVp | 1550kVp |
| iii) | One-minute power frequency dry withstand voltage (rms) | 830kV | 630kV | 830kV |
| 6. | Corona extinction voltage | 508 kV | 320kV | 508 kV |
| 7. | Max. radio interference voltage for frequency between 0.5 MHz and 2 MHz | 2500 micro-volts at 508 kV rms | 1000 micro-volts at 266kV rms | 2500 micro-volts at 508 kV rms |
| 8. | Minimum creepage distance for insulator string/ longrod insulators/ outdoor bushings | 24800 mm (31mm/kV) | 13020 mm (31mm/kV) | 24800 mm (31mm/kV) |
| 9. | Minimum creepage distance for switchyard equipment | 20000 (25mm/kV) | 10500mm (25mm/kV) | 20000 (25mm/kV) |
| 10. | Max. fault current | 50 kA | 63 kA | 50 kA |
| 11. | Duration of fault | 1 sec | 1 Sec | 1 sec |

B.1.2	Switching Scheme

The switching schemes, as mentioned below, shall be adopted at various voltage levels of substation/switchyard:

| Substation | 765kV side | 400kV side | 220kV side (Future) |
| --- | --- | --- | --- |
| 765/400/220kV Beawar s/s | One & Half breaker (AIS) | One & Half breaker (AIS) | Double Main & Transfer (AIS) |
| 765kV Fatehgarh-3 s/s | One & Half breaker (AIS) | ---- | ---- |

Notes: -

- At 765kV & 400kV voltage level, each circuit of a double circuit transmission line (originating from same substation) shall be terminated in different diameters.

- Transformers and bus reactors of same HV rating shall be placed in different diameters (i.e. transformers of same HV rating shall not be in the same diameter and similarly, bus reactors of same HV rating shall also not be in the same diameter).

- TSP shall also keep space provision for future 220kV Bus Coupler bay and 220kV Transfer Bus Coupler bay.

- Connection arrangement of Switchable Line reactors shall be such that it can be used as Line rector as well as Bus reactor with suitable NGR bypass arrangement.

- 765kV, 1-phase circuit breaker is under present scope of work for utilizing existing 110 MVAR (supplied with bus reactor) spare Reactor for switchable line reactor of Beawar 765kV D/C line (at Fatehgarh-3).

B.2.0	Substation Equipment and facilities (Voltage level as applicable):

The switchgear shall be designed and specified to withstand operating conditions and duty requirements. All equipment shall be designed considering the following capacity.

| Sl. No | Description of bay | 765/400kV Beawar |  | Extn. of 765kV Fatehgarh-3 s/s |
| --- | --- | --- | --- | --- |
|  |  | 765kV | 400kV | 765kV |
| 1. | Bus Bar | 4000 A | 4000 A | 4000 A |
| 2. | Line bay | 3150 A | 3150 A | 3150 A |
| 3. | ICT bay | 3150 A | 3150 A | 3150 A |
| 4. | Bus Reactor bay | 3150 A | 3150 A | 3150 A |
| 5. | Switched Line Reactor Bay | 3150 A | -- | 3150 A |

B.2.1 	(765/3)/(400/3)/33 kV, Single Phase Autotransformer

500 MVA, (765/3)/(400/3)/33kV, 1-phase Transformer (including arrangement for 3-phase bank formation of 1500 MVA) shall conform to CEA’s “Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV and above)”  as amended upto date available on CEA website

Spare 1-phase Transformer unit shall be placed and connected in such a way that in case of fault in any unit of any of the transformer banks (including for future transformer banks) can be replaced by spare unit without physically moving it.

B.2.2	(765/3) kV, Single Phase Shunt Reactor

110 MVAR, 765/3 kV, 1-Phase Reactor (including arrangement for 3-phase bank formation of 330 MVAR) shall conform to CEA’s “Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV and above)”  as amended upto date available on CEA website

Spare 1-phase Shunt Reactor unit shall be placed and connected in such a way that the spare unit can be utilized for all the bus and line reactor banks (including for future reactor banks) without its physical movement.

- Neutral Grounding Reactor (NGR) and Surge Arrester for 765 kV Line Reactors (as applicable)

The neutral of the line reactors (wherever provided) shall be grounded through adequately rated Neutral Grounding Reactors (NGR) to facilitate single phase auto-reclosure, provided that the NGR shall be provided with bypass arrangement through a breaker so that the line reactor can be used as Bus reactor as and when required. The neutral of bus reactor shall be solidly grounded. The ohmic value of NGR for each circuit at both ends of 765kV D/c Fatehgarh-3– Beawar S/s shall be 450 ohms. NGR shall be oil filled or dry type air core for outdoor application. NGR shall conform to CEA’s “Standard specifications and technical parameters of transformers and reactors (66kV and above)”. Technical parameters of NGR shall be as specified in Annexure-A of abovementioned document. The surge arresters (rated voltage of arrester in co-ordination with ohmic value of NGR shall be decided by the TSP) shall be provided & physically located between the neutral of shunt reactor (brought out at 145kV class bushing) and neutral grounding reactor. The surge arresters shall be of heavy duty station class gapless Metal oxide (ZnO) type conforming in general to IEC-60099-4. Arresters shall be hermetically sealed units, of self-supporting construction, suitable for mounting on structures.

B.2.3	420kV, 3-phase, Shunt Reactor

125 MVAR, 420kV, 3-Phase Reactor shall conform to CEA’s “Standard Specifications and Technical Parameters for Transformers and Reactors (66 kV and above)” available on CEA website.

B.2.4	765kV and 400kV AIS Substation equipment (as applicable)

B.2.4.1	Circuit Breakers (AIS)

The circuit breakers and accessories shall conform to IEC: 62271-100, IEC: 62271-1 and shall be of SF6 Type. The circuit breakers shall be of class C2-M2 (as per IEC) with regard to restrike probability during capacitive current breaking and mechanical endurance. The rated break time shall not exceed 40ms for 765kV & 400kV circuit breakers. The Circuit breakers controlling 765kV lines shall be provided either with pre-insertion closing resistor of about 450 ohms maximum with 9 ms insertion time or with Controlled Switching Device. The Circuit breakers controlling 400kV lines of more than 200 km length shall be provided either with pre insertion closing resistor of about 400 ohms maximum with 8 ms insertion time or with Controlled Switching Device (CSD). 765kV and 400kV Circuit breakers shall be provided with single phase and three phase auto reclosing. The short line fault capacity shall be same as the rated capacity and this is proposed to be achieved without use of opening resistors. The controlled switching device shall be provided in Circuit breakers of switchable line reactor and in Main & Tie circuit breakers of line with non-switchable line reactors and Bus reactors and 765/400kV Transformers.

B.2.4.2	Isolators (AIS)

The isolators shall comply to IEC 62271-102 in general.765kV Isolator design shall be double break or vertical break or knee-type. 400kV shall be double break type. All Isolators and earth switches shall be motor operated. Earth switches shall be provided at various locations to facilitate maintenance. Isolator rated for 765kV and 400kV shall be of extended mechanical endurance class - M2 and suitable for bus transfer current switching duty as per IEC-62271-102. Main blades and earth blades shall be interlocked and interlock shall be fail safe type. 765kV & 400kV earth switches for line isolator shall be suitable for induced current switching duty as defined for Class-B.

B.2.4.3	Current Transformers (AIS)

Current Transformers shall comply with IEC 61869 in general. All ratios shall be obtained by secondary taps only. Generally, Current Transformers (CT) for 765kV & 400kV shall have six cores (four for protection and two for metering). The burden and knee point voltage shall be in accordance with the requirements of the system including possible feeds for telemetry. Accuracy class for protection core shall be PX and for metering core it shall be 0.2S. The rated burden of cores shall be closer to the maximum burden requirement of metering & protection system (not more than 20VA for metering core) for better sensitivity and accuracy. The instrument security factor shall be less than 5 for CTs upto 400kV and less than 10 for CTs of 765kV voltage class.

B.2.4.4	Capacitive Voltage Transformers (AIS)

Capacitive Voltage transformers shall comply with IEC 61869 in general. These shall have three secondaries out of which two shall be used for protection and one for metering. Accuracy class for protection cores shall be 3P and for metering core shall be 0.2. The Capacitive voltage transformers on lines shall be suitable for Carrier Coupling. The Capacitance of CVT for 400kV shall be of 4400/8800 pF depending on PLCC requirements whereas the Capacitance of CVT for 765kV shall be 8800 pF. The rated burden of cores shall be closer to the maximum burden requirement of metering & protection system (not more than 50VA for metering core) for better sensitivity and accuracy.

B.2.4.5	Surge Arresters (AIS)

624kV & 336kV Station High (SH) duty gapless type Surge arresters with thermal energy (Wth) of minimum 13 kJ/kV and 12 kJ/kV conforming to IEC 60099-4 in general shall be provided for 765 kV and 400 kV systems respectively. Other characteristics of Surge arrester shall be chosen in accordance with system requirements. Surge arresters shall be provided near line entrances, Transformers & Reactor so as to achieve proper insulation coordination. Surge Arresters shall be provided with porcelain/ polymer housing fitted with pressure relief devices. A leakage current monitor with surge counter shall be provided with each surge arrester.

B.2.5	Protection Relaying & Control System

The protective relaying system proposed to be provided for transmission lines, auto-transformers, reactors and bus bars to minimize the damage to the equipment in the events of faults and abnormal conditions, is dealt in this section. All main protective relays shall be numerical type with IEC 61850 communication interface and should have Interoperability during integration of numerical relays to communicate over IEC61850 protocol with RTU/SAS/IEDs of different OEMs All numerical relays shall have built in disturbance recording feature.

The protection circuits and relays of transformer and reactor shall be electrically and physically segregated into two groups each being independent and capable of providing uninterrupted protection even in the event of one of the protection groups failing, to obtain redundancy, and to take protection systems out for maintenance while the equipment remains in service.

  - Transmission Lines Protection

765kV and 400kV lines shall have Main-I numerical three zone distance protection scheme with carrier aided inter-tripping feature. 765kV and 400kV lines shall also have Main-II numerical distance protection scheme like Main-I but from different make that of Main-I. The Main-I and Main-II protection relays of same make may be provided only if they are of different hardware & manufacturing platform or different principle of operation.

However, Line Current Differential relay (with back up distance protection feature) as Main–I and Main-II shall be considered at both ends for short lines (line length below 30kM) having Fiber Optic communication link. Differential relay at remote end shall be provided by the TSP. Associated power & control cabling and integration with SAS at remote end shall be provided by respective bay owner.

In case of loop in loop out of transmission lines, the existing protection scheme shall be studied and suitable up-gradation (if required) shall be carried out.

Further, all 765kV and 400kV lines shall be provided with single and three phase auto-reclosing facility to allow reclosing of circuit breakers in case of transient faults.  These lines shall also be provided with distance to fault locators to identify the location of fault on transmission lines.

All 765kV and 400kV lines shall also be provided with two stages over voltage protection. Over voltage protection & distance to fault locator may be provided as in-built feature of Main-I & Main-II protection relays. Auto reclose as built-in function of Bay Control Unit (BCU) is also acceptable.

The Main-I and Main-II protection relays shall be fed from separate DC sources and shall be mounted in separate panels.

For 765kV and 400kV transmission lines, directional IDMT earth fault relay should be provided as standalone unit or in-built feature of Main-I and Main -II feature.

  - Auto Transformer Protection

These shall have the following protections:

i)   	Numerical Differential protection

ii)  	Numerical Restricted earth fault protection

iii) 	Numerical Back-up Over-current and earth fault protection on HV & MV side

iv) 	Numerical Over fluxing protection on HV & MV side

v)  	Numerical Overload alarm

Further, Numerical Back-up Over-current and earth fault protection on HV & MV side of autotransformer shall not be combined with other protective functions in the main relays and shall be independent relays. Besides these, power transformers shall also be provided with Buchholz relay, protection against high oil and winding temperature and pressure relief device etc.

Suitable monitoring, control (operation of associated circuit breaker & isolator) and protection for LT auxiliary transformer connected to tertiary winding of auto-transformer for the purpose of auxiliary supply shall be provided. The Over current and other necessary protection shall be provided for the auxiliary transformer. These protection and control may be provided as built in feature either in the bay controller to be provided for the auxiliary system or in the control & protection IEDs to be provided for autotransformer.

  - 765kV & 400kV Reactor Protection

Reactor shall be provided with the following protections:

i)   	Numerical Differential protection.

ii)  	Numerical Restricted earth fault protection

iii) 	Numerical Back-up impedance protection

Besides these, reactors shall also be provided with Buchholz relay, MOG with low oil level alarm, protection against oil and winding temperatures & pressure relief device, etc.

  - Bus Bar Protection

The high-speed low impedance type bus bar differential protection, which is essential to minimize the damage and maintain system stability at the time of bus bar faults, shall be provided for 765kV and 400kV buses. Duplicated bus bar protection is envisaged for 765kV & 400kV bus-bar protection. Bus bar protection scheme shall be such that it operates selectively for each bus and incorporate necessary features required for ensuring security. The scheme shall have complete bus bar protection for present as well as future bays envisaged i.e. input / output modules for future bays shall also be provided.

Bus Bar protection system for new substation shall be de-centralized (distributed) type.

In case, the bus section is provided, then each side of bus section shall have separate set of bus bar protection schemes.

For existing substations, the existing bus bar protection shall be augmented as per requirement.

  - Local Breaker Back up Protection

This shall be provided for each 765kV and 400kV circuit breakers and will be connected to de-energize the affected stuck breaker from both sides.

Notes:

- LBB & REF relays shall be provided separately from transformer differential relay.

- LBB relay may also be provided as built-in protection function of distributed bus bar protection scheme; however, in such case separate LBB relay shall be provided for tie bays (in case of One and Half breaker scheme).

- Over fluxing & overload protection can be provided as built-in feature of differential relay.

- In 765kV & 400kV switchyard, if spare bay of half diameter is identified as future, Tie CB relay panel shall be with Auto-reclosure feature.

B.2.6	Substation Automation System

- For all the new substations, state of art Substation Automation System (SAS) conforming to IEC-61850 shall be provided. The distributed architecture shall be used for Substation Automation system, where the controls shall be provided through Bay control units. The Bay control unit is to be provided bay wise for voltage level 220kV and above. All bay control units as well as protection units are normally connected through an Optical fiber high speed network. The control and monitoring of circuit breaker, dis-connector, re-setting of relays etc. can be done from Human Machine Interface (HMI) from the control room.

The functions of control, annunciation, disturbance recording, event logging and measurement of electrical parameters shall be integrated in Substation Automation System.

At new substations, the Substation Automation System (SAS) shall be suitable for operation and monitoring of the complete substation including proposed future bays/elements.

In existing substations with Substation automation system (SAS), augmentation of existing SAS shall be done for bays under present scope.

In existing Substations where Substation automation is not provided, control functions shall be done through control panels.

Necessary gateway & modems (as required) shall be provided to send data to RLDC/SLDC as per their requirement. Any augmentation work at RLDC/SLDC is excluded from TSP’s scope. However, all the configuration work at substation end required to send data to RLDC/SLDC shall be in the scope of TSP.

- Time synchronisation equipment

Time synchronization equipment complete in all respect including antenna, cable, processing equipment required to receive time signal through GPS or from National Physical Laboratory (NPL) through INSAT shall be provided at new substations. This equipment shall be used to synchronize SAS & IEDs etc.

B.3.0	Substation Support facilities

Certain facilities required for operation & maintenance of substations as described below shall be provided at new substation. In existing substation, these facilities have already been provided and would be extended/ augmented as per requirement.

B.3.1	AC & DC power supplies

For catering the requirements of three phase & single-phase AC supply and DC supply for various substation equipment (for present and future scope), the following arrangement is envisaged: -

- For LT Supply at each new Substation, two (2) nos. of auxiliary Transformers (minimum 800kV for substation with highest voltage rating as 765kV and minimum 630kVA for substations with highest voltage rating as 400kV) fed from independent sources shall be provided as per the CEA (Technical Standards for Connectivity to the Grid) Regulations, 2007.

Metering arrangement with Special Energy Meters (SEMs) shall be provided by TSP at 33kV tertiary of Transformer for drawing auxiliary supply at new substation. Such SEMs shall be provided by CTU at the cost of the TSP. Accounting of such energy drawn by the TSP shall be done by RLDC/RPC as part of Regional Energy Accounting.

Additionally, Active Energy Meters may be provided at the same point in the 33kV tertiary of Transformer by local SEB/DISCOM for energy accounting.

- 2 sets of 220V battery banks for control & protection and 2 sets of 48V battery banks for PLCC/ communication equipment shall be provided at each new Substation. Each battery bank shall have a float-cum-boost charger. At new substation, sizing of 220 V battery and battery charger shall be done based on the number of bays specified (including future bays) as per CEA Regulations and relevant IS. 2 sets of 48 V battery banks for PLCC and communication equipment shall be provided each new substation with at least 10-hour battery backup and extended backup, if required. 48 V can be achieved from 220 V battery bank also, if desired, without compromising backup time.

- Suitable AC & DC distribution boards and associated LT Switchgear shall be provided at new substation.

For new substation, following switch boards shall be considered with duplicate supply with bus coupler/ sectionalizer and duplicate outgoing feeders except for Emergency lighting distribution board which shall have only one incoming feeder:

  - 415V Main Switch board – 1 nos.

  - AC distribution board – 1 nos.

  - Main lighting distribution board – 1 no.

  - Emergency lighting distribution board – 1 no.

  - 220 Volt DC distribution board – 2 nos.

  - 48 Volt DC distribution board – 2 nos.

Sizing of LT Switchgear shall be suitable to cater the requirement for all present and future bays. AC & DC distribution boards shall have modules for all the feeders (including future as specified).

- At new Substation, one no. of DG set (minimum 500 kVA for substations with highest voltage rating as 765kV and minimum 250kVA for substations with highest voltage rating as 400kV) shall be provided for emergency applications.

- For substation extensions, existing facilities shall be augmented as required.

B.3.2	Fire Fighting System

Fire-fighting system for substation including transformer & reactor shall conform to CEA (Measures Relating to Safety & Electric Supply) Regulations.

Further, adequate water hydrants and portable fire extinguishers shall be provided in the substations. The main header of firefighting system shall be suitable for extension to bays covered under the future scope; necessary piping interface in this regard shall be provided.

At existing substations, the fire-fighting systems as available shall be extended to meet the additional requirements.

B.3.3	Oil evacuating, filtering, testing & filling apparatus

To monitor the quality of oil for satisfactory performance of transformers, shunt reactors and for periodical maintenance necessary oil evacuating, filtering, testing and filling apparatus would be provided at new substations. Oil storage tanks of adequate capacities for storage of transformer oil would be provided.

B.3.4	Illumination

Normal & emergency AC & DC illumination shall be provided adequately in the control room & other buildings of the substation. The switchyard shall also be provided with adequate illumination.

Lighting of the entire control room building, fire-fighting pump house, other building (if any) and switchyard shall be done by LED based low power consumption luminaires.

B.3.5	Control Room

For new substation, substation control room shall be provided to house substation work stations for station level control (SAS) alongwith its peripheral and recording equipment, AC & DC distribution boards, DC batteries & associated battery chargers, Fire Protection panels, Telecommunication panels & other panels as per requirements. Air conditioning shall be provided in the building as functional requirements. Main cable trenches from the control room shall have adequate space provision for laying of cables from control room for all the future bays also.

At existing substations, the adequacy of size of control room shall be ascertained and the same shall be augmented as per requirement.

B.3.6	Control Concept

All the EHV circuit breakers in substation/switching stations shall be controlled and synchronized from the switchyard control room/remote control center. Each breaker would have two sets of trip circuits which would be connected to separate DC supplies for greater reliability. All the isolators shall have control from remote/local whereas the earth switches shall have local control only.

B.3.7	Visual monitoring system (VMS) for watch and ward of substation premises:

Visual monitoring system for effective watch and ward of substation premises shall cover all the transformers and reactors, all other major AIS Equipment (such as CB, isolators, CT, CVT, SA etc. as applicable), GIS bays, panel room, all the gates of switchyard and all entry and exit points of control room building and accordingly the location of cameras shall be decided. The camera shall be high definition color CCD camera with night vision feature. The VMS data partly/completely shall be recorded (minimum for 15 days) at least @25fps (or better) and stored on network video recorder. The system shall use video signals from various cameras installed at different locations, process them for viewing on workstations/monitors in the control room and simultaneously record all the cameras.

Mouse/keyboard controllers shall be used for pan, tilt, zoom and other functions of the desired camera. The Visual Monitoring System shall have provision of WAN connectivity for remote monitoring.

All camera recordings shall have Camera ID & location/area of recording as well as date/time stamp. The equipment should generally conform to Electromagnetic compatibility requirement for outdoor equipment in EHV substation.

At existing substations, the visual monitoring system if available shall be augmented as per existing or better specification as required.

B.4	General Facilities

- Line Gantry/Towers are envisaged for bays under present scope only. However, for adjacent future line bay, tower shall be designed for extension (considering Quad conductors for 765kV & 400kV future lines) wherever applicable.

- Bay extension works at existing substation shall be executed by TSP in accordance with the requirement/provisions mentioned above. However, interface points shall be considered keeping in view the existing design/arrangement at the substation.

- TSP has to arrange for construction power and water on its own.

- All outdoor steel structures including anchor/foundation bolts shall be fully galvanized. The weight of the zinc coating shall be at least 610 gm/sq.m, however, for coastal/creek regions it shall be at least 900 gm/sq.m.

- In 765kV & 400kV switchyard, if spare bay of half diameter is identified as future, all the equipment for Tie & Future bay shall be designed considering the current rating of line bay i.e. 3150A.

- Boundary wall shall be brick masonry wall with RCC frame or Stone masonry wall or Precast RCC wall under present scope along the property line of complete substation area including future switchyard area to prevent encroachment and unauthorized access. Minimum height of the boundary wall shall be of 1.8 m from finished ground level (FGL) as per CEA Measures Relating to Safety and Electric Supply Regulations.

B.5	EXTENSION OF EXISTING SUBSTATION

The following drawings/details of existing substation is attached with the RFP documents for further engineering by the bidder:

| Sl. No. | Drawing Title | Drawing No./Details | Rev. No. |
| --- | --- | --- | --- |
| A. | 765kV Fatehgarh-3 (AIS) S/S |  |  |
| 1.0 | Single Line Diagram | C/ENGG/SS/FATEHGARH-3/SLD/01 | 02 |
| 2.0 | General Arrangement | C/ENGG/SS/FATEHGARH-3/GA/01 | 01 |
| 3.0 | Earthmat Layout | KPTL/PGCIL/WO-SS-033/02E/RGH-II/009 | 01 |
| 4.0 | Visual Monitoring System | The drawings are yet to be finalized by developer. | - |
| 5.0 | Bus Bar Protection (400 kV System) | The drawings are yet to be finalized by developer. | - |
| 6.0 | Substation Automation System (SAS) | GE Make, KZ3DSA1 | C |

Bidder is also advised to visit the substation sites and acquaint themselves with the topography, infrastructure such as requirement of roads, cable trench, drainage etc. and also the design philosophy.

SPECIFIC TECHNICAL REQUIREMENTS FOR COMMUNICATION

The communication requirement shall be in accordance to CEA (Technical Standards for Communication System in Power System Operations) Regulations, 2020, CERC (Communication System for inter-State transmission of electricity) Regulations, 2017, and CEA (Cyber Security in Power Sector) Guidelines, 2021, all above documents as amended from time to time.

The protections for transmission line and the line compensating equipment shall have hundred percent back up communication channels i.e. two channels for tele- protection in addition to one channel for speech plus data for each direction

In order to meet the requirement for grid management and operation of substations, Transmission Service Provider (TSP) shall provide the following:

C.1.0   	LILO of both circuits of Ajmer – Chittorgarh 765kV D/c at Beawar

On LILO of both circuits of Ajmer – Chittorgarh 765kV D/c at Beawar, TSP to supply, install & commission OPGW and earthwire as per Tower Configurations:

- For Multi Circuit Tower Configuration: Two (2) no. OPGW cable containing 24 Fibres (24F) on both the Earthwire peaks

- For Double Circuit Tower configuration (for both Loop In and Loop Out portion): One (1) no. OPGW cable containing 24 Fibres (24F) to be installed on one earthwire peak & conventional earthwire on other earthwire peak for both Loop In and Loop Out Lines.

The TSP shall install OPGW cables from Gantry of Beawar S/s up to the LILO tower with all associated hardware including Vibration Dampers, LILO Tower, mid-way & gantry Joint Boxes (called OPGW Hardware hereafter) and finally terminate in Joint Boxes at Beawar. If repeater required to meet the link budget requirement of Ajmer – Beawar & Beawar – Chittorgarh link the same shall be provided by TSP.

TSP shall finalize the location of repeater station depending upon the actual site conditions.  Further TSP shall comply to the requirements mentioned as per Appendix-F.1.

Maintenance of OPGW Cable and OPGW Hardware shall be responsibility of TSP.

C.2.0   	LILO of Kota – Merta 400 kV at Beawar

On LILO of Kota – Merta 400 kV line at Beawar, TSP shall supply, install & commission Two (2) no. OPGW cable containing 24 Fibres (24F) on both the E/W peaks of tower.

The TSP shall install OPGW cables from gantry of Beawar S/s up to the LILO tower with all associated hardware including Vibration Dampers, LILO tower, mid-way & gantry Joint Boxes (called OPGW Hardware hereafter) and finally terminate in Joint Boxes at Beawar. If repeater required to meet the link budget requirement of Kota – Beawa	r & Beawar – Merta link the same shall be provided by TSP.

TSP shall finalize the location of repeater station depending upon the actual site conditions. Further TSP shall comply to the requirements mentioned as per Appendix-F.1.

Maintenance of OPGW Cable and OPGW Hardware shall be responsibility of TSP.

C.3.0   	Fatehgarh-3 – Beawar 765 kV D/c line

On Fatehgarh-3 – Beawar 765 kV D/c line, TSP shall supply, install & commission One (1) no. OPGW cable containing 24 Fibres (24F) on one E/W peak and conventional earth wire on other E/W peak.

The TSP shall install this OPGW from gantry of Fatehgarh -3 up to the gantry of Beawar S/s with all associated hardware including Vibration Dampers, mid-way & gantry Joint Boxes (called OPGW Hardware hereafter) and finally terminate in Joint Boxes at end Substations. Repeater/s are required to meet link budget requirement of Fatehgarh-3 – Beawar link.

TSP shall finalize the location of repeater station depending upon the actual site conditions.  Further TSP shall comply to the requirements mentioned as per Appendix-F.1.

C.4.0 	Establishment of 2x1500MVA 765/400kV Substation at suitable location near Beawar along with 2x330 MVAr 765kV Bus Reactor & 2x125 MVAr 420kV Bus Reactor

- TSP shall supply, install & commission 2 no. FODP (96 F) alongwith panel and approach Cable (24F each) with all associated hardware fittings from gantry tower to Control Room for all the incoming lines envisaged under the present scope.

- TSP shall supply, install & commission One or more STM-16 (FOTE) equipment alongwith panel/s supporting minimum seven (7) directions with MSP (Multiplex Section Protection – 1+1). These directions shall exclude protected (1+1) local patching among equipment (if any). Communication equipment shall be provided with necessary interfaces to meet the voice and data communication requirement among Beawar, Ajmer, Chittorgarh, Kota, Merta, Repeater Stations & Fatehgarh-3 S/s. TSP to also provide suitable optical interfaces/equipment at Fatehgarh-3, Ajmer, Chittorgarh, Merta, Kota Substations FOTE to meet link budget requirement for connectivity with Beawar Station if required. The suitable DC Power Supply and backup to be provided for communication equipment.

- FODP & FOTE equipment with panels shall be provided in Control Room of Beawar PS. FOTE & FODP Eq can be accommodated in same panel to optimize space.

- The new communication equipment under the present scope shall be compatible for integration with existing regional level centralized NMS. The local configuration of the new communication equipment shall be the responsibility of TSP. The configuration work in the existing centralized NMS for integration of new Communication equipment shall be done by Regional ULDC Team, however all the necessary support in this regard shall be ensured by TSP.

- TSP shall supply, install & commission required no. of Phasor Measurement Units (PMUs) for all 400kV and above voltage line including STATCOM bays (under the scope of this project) at Beawar S/s, these PMUs shall support latest IEEE C-37.118 protocols. These PMUs shall be provided with GPS clock and LAN switch and shall connect with LAN switch of control room with Fibre Optic cable. These PMUs shall be connected with the FOTE at Substation for onwards data transmission to the PDC (Phasor Data Concentrator) located at respective RLDC. However, configuration work in existing PDC at RLDC for new PMU integration is not in scope of TSP (shall be done by respective RLDC), however all the necessary support in this regard shall be ensured by TSP.

- TSP shall supply, install & commission Firewall in redundant mode (1+1) in line with the specification attached at Annexure F.1

- The maintenance of all the communication equipment including FOTE, FODP, approach cable, PMUs, DCPS alongwith Battery Bank shall be the responsibility of TSP.

C.5.0   	PLCC & PABX:

Power line carrier communication (PLCC) equipment complete for speech, tele-protection commands and data channels shall be provided on each transmission line. The PLCC equipment shall in brief include the following: -

- Coupling device, line traps, carrier terminals, protection couplers, HF cables, PABX (if applicable) and maintenance and testing instruments.

- At new substation, a telephone exchange (PABX) of 24 lines shall be provided at as means of effective communication among various buildings of the substation, remote end substations and with control centers (RLDC/SLDC) etc.

- Coupling devices shall be suitable for phase to phase coupling for 400kV Transmission lines. The pass band of coupling devices shall have sufficient margin for adding communication channel in future if required. Necessary protection devices for safety of personnel and low voltage part against power frequency voltages and transient over voltage shall also be provided.

- The line traps shall be broad band tuned suitable for blocking the complete range of carrier frequencies. Line Trap shall have necessary protective devices such as lightning arresters for the protection of tuning device. Decoupling network consisting of line traps and coupling capacitors may also be required at certain substation in case of extreme frequency congestion.

- The carrier terminals shall be of single side-band (SSB) amplitude modulation (AM) type and shall have 4 kHz band width. PLCC Carrier terminals and Protection couplers shall be considered for both ends of the line.

- PLCC equipment for all the transmission lines covered under the scheme (consisting of one set of analog PLCC channel along with circuit protection coupler and one set of Digital protection coupler for both ends) shall be provided by TSP. CVT & Wave trap for all the line bays under present scope shall be provided by TSP.

- TSP shall provide/ undertake necessary addition/ modification/ shifting/ re-commissioning etc. of PLCC equipment due to LILO of transmission lines (wherever applicable). The make & model of existing PLCC system is as follows:

| Sl. No. | Name of the existing line | Make & Model of PLCC |
| --- | --- | --- |
| 1. | 765kV Ajmer- Chittorgarh D/c line | Analog PLCC Make – ABB Model – ETL-81 + NSD50 Digital PLCC Make – ABB Model – NSD-70D |
| 2. | 400kV Kota – Merta line | Make – ABB Model – ETL-41 |

- All other associated equipment like cabling, coupling device and HF cable shall also be provided by the TSP.

- 2 sets of 48V battery banks for PLCC and communication equipment shall be provided at each new Substation with at least 10 hours battery backup and extended backup, if required.

C.7.0 Next Generation Firewall (NGFW) Requirement

- TSP shall provide 2 nos. Next Generation Firewalls (NGFW); one No. Main & one No. Standby having electrical ethernet interfaces/ports and placed between FOTE & SAS gateway/s at the substation. All ethernet based applications (e.g. PMU, AMR, VOIP, SAS/SCADA etc.) shall be terminated in the firewall ports directly. Each port of firewall shall work as a separate zone. Firewall shall be hardware based with functionality of Block/Allow/drop and IPSec VPN (network encryption).

- Minimum 16 Nos. of ports/interfaces shall be provided in each firewall (i.e. Main & Standby) TSP can use either single firewall or multiple firewalls to meet this interfaces requirement, each for main as well as standby firewall. Minimum throughput of firewall shall be 300 Mbps.

- The Firewall shall be managed/ configured as standalone at present and shall also have compatibility to manage/configure through Centralized Management Console (CMC) remotely in future.

- OEM Support on 24x7 basis for 7 years shall be provided for all the functions & features of the Firewall.

- Firewall shall be tested and certified for ISO15408 Common Criteria for least EAL4+. Further, the OEM must certify that it conforms to Secure Product Development Life Cycle requirements as per IEC62443-4-1. The firewall shall generate reports for NERC-CIP Compliance.

The specifications for the firewalls are given at Annexure-F.1 and schematic diagram showing firewall placement given at Figure F.1.

Appendix-F.1

Repeater Requirements

- If the repeater location is finalized in the Control Room of a nearby substation, TSP shall provide 1 no. OPGW (48F) on a single Earthwire peak with OPGW Hardware & mid-way Joint Boxes etc. of the line crossing the main line and 1 no. Approach Cable (48F) with all associated hardware fittings, to establish connectivity between crossing point of main transmission line up to the repeater equipment in substation control room.

TSP shall co-ordinate for Space & DC power supply sharing for repeater equipment.

TSP shall provide FODP, FOTE (with STM-16 capacity) with suitable interfaces require   for link budget of respective link.

OR

- If the repeater location is finalized in the nearby substation premises, the TSP shall identify the Space for repeater shelter in consultation with station owner. Further TSP shall provide 1 no. OPGW (48F) on a single Earthwire peak with OPGW Hardware & mid-way Joint Boxes etc. of the line crossing the main line and 1 no. Approach Cable (48F) / UGFO (48F) with all associated hardware fittings, to establish connectivity between crossing point of main transmission line up to the substation where the repeater shelter is to be housed. TSP shall provide repeater shelter along with FODP, FOTE (with STM-16 capacity) with suitable interfaces require for link budget of respective link, reliable power supply provisioning for AC and DC supply, battery bank, Air Conditioner and other associated systems.

OR

- If the repeater location is finalized on land near the transmission tower. TSP shall make the provisions for Land at nearby tower for repeater shelter. Further TSP shall provide 1 no. Approach Cable (48F) / UGFO (48F) with all associated hardware fittings to establish connectivity up to the location of repeater shelter.

TSP shall provide repeater shelter along with FODP, FOTE (with STM-16 capacity) with suitable interfaces require for link budget of respective link, reliable power supply provisioning for AC and DC supply, battery bank, Air Conditioner and other associated systems

Maintenance of OPGW Cable and OPGW Hardware, repeater equipment & items associated with repeater shelter shall be responsibility of TSP.

Note: Existing Station owner/s to provide necessary support to integrate different equipment & applications of new extended bays with the existing substation e.g. Communication (through FOTE), PMUs, Voice etc. for smooth operation and monitoring of new added grid elements.

Figure F.1

Annexure F.1

Specifications of Next Generation Firewall (NGFW)

      - NGFW shall have following features including but not limited to:

Encryption through IPSec VPN (Virtual Private Network), Deep Packet Inspection (DPI), Denial of service (DoS) & Distributed Denial of Service (DDoS) prevention, Port Block/ Allow, rules/ policies for block/allow, IP (Internet Protocol) & Media Access Control (MAC) spoofing protection, threat detection, Intrusion Prevention System (IPS), Anti-Virus, Anti-Spyware, Man In The Middle (MITM) attack prevention.

      - The proposed firewall shall be able to handle (alert, block or allow) unknown /unidentified applications e.g. unknown TCP & UDP packets. It shall have the provision to define application control list based on application group and/or list.

      - Firewall shall have feature and also have capability to update the definition/ Signatures of Anti-Virus online as well as offline. Firewall shall also be compatible to update the definitions/signatures through CMC. There shall be a defined process for security patching and firmware up-gradation. There shall be a feature to field validate firmware checksum. The same shall also be validated before using the OEM provided file/binary in the process of firmware up-gradation and security patching

      - Firewall shall have Management Console port to configure remotely.

      - Firewall shall be EMI/EMC compliant in Substation environment as per IEC 61850-3.

      - Firewall shall be rack mounted in existing standard equipment cabinets.

      - Firewall shall have support of SCADA applications (IEC-60870-5-104), ICCP, PMU (IEEE C37.118), Sub-Station Automation System (IEC 61850), Ethernet and other substation environment protocols.

      - Client based Encryption/ VPN must support different Operating System platforms e.g. Windows, Linux & Mac.

      - The solution must have content and comprehensive file detection policies, blocking the files as function of their types, protocols and directions.

      - Firewall shall have logging facility as per standard logs/events format. Firewall shall have features to export the generated/stored logs/events in csv (Comma Separated Value) and also any other standard formats for offline usage, analysis and compliance.

Firewall shall have suitable memory architecture and solution to store and be enable to export all logs/events for a period of last 90 days at any given time.

      - Firewall shall have features and be compatible with local as well as central authentication system (RADIUS, LDAP, or TACACS+) for user account and access right management. It shall also have Role Based User management feature.

      - Firewall shall have the capability to configure sufficient number of VLANs.

      - Firewall shall have the capability to support sufficient number of sessions.

      - Firewall shall have provision to configure multiple IP Sec VPNs, at least 100 nos., (one-to-many or many-to-one). Shall support redundant operation with a similar router after creation of all the IP Sec VPN. IPSec VPN shall support encryption protocols as AES128, AES256 and hashing algorithms as MD5 and SHA1. IPSec VPN throughput shall support at least 300 Mbps

      - Firewall shall be capable of SNMP v3 for monitoring from Network Management system. It shall also have SNMPv3 encrypted authentication and access security

      - Firewall shall support in Active/Passive or Active-Active mode with High Availability features like load balancing, failover for firewall and IPsec VPN without losing the session connectivity.

      - Firewall should have integrated traffic shaping (bandwidth, allocation, prioritisation, etc.)  functionality

      - Firewall shall support simultaneous operation with both IPv4 and IPv6 traffic

      - Firewall shall be compatible with SNTP/NTP or any other standards for clock synchronization

      - Firewall shall have the features of port as well as MAC based security

      - Firewall shall support exporting of logs to a centralized log management system (e.g. syslog) for security event and information management.

      - Firewall time shall be kept synchronised to official Indian Timekeeping agency, time.nplindia.org.

      - Firewall product shall be provided with all applicable updates at least until 36 months since the applicable date of product shipping to the concerned utility.

Figure- F.2

Specific Technical Requirement for STATCOM

Appendix 1

- Introduction:

This technical specification for a Static Synchronous Compensator (STATCOM) Station consists of STATCOM, Mechanically Switched Capacitors (MSCs) and Mechanically Switched Reactors (MSRs) (to be installed at MV bus) including associated coupling Transformer (rated 400/xx kV) and other equipment connected to the 400 kV bus. MV voltage level (xx kV) of the coupling Transformer can be chosen by the TSP to optimize the offered solution which meets functional requirement of this Technical Specification.

The STATCOM station shall operate asymmetrically in the leading and lagging MVAR region as applicable to reach the dynamic range specified. The purpose of the STATCOM station is to regulate the voltage of 400 kV Bus [Point of Common Coupling (PCC)]. The Configuration and the nominal rating of the STATCOM station is specified in this document.

The main building block of the STATCOM should be single phase VSC based convertor valve (multi-level) operating in a way to eliminate or minimize ac filter requirement to High pass filter only and connected to the xx kV bus through air core reactors.

  - Definitions and Abbreviations

For the purpose of this specification, the following definitions / abbreviations are used:

PCC: Point of Common Coupling. The connection point between the STATCOM and the power system at which performance requirements are defined.

Reference Voltage (Vref): The Point on the voltage/current (V/I) characteristic where the static synchronous compensator (STATCOM) is at zero output (i.e. where no reactive power is absorbed from or supplied to the transmission system where the voltage is controlled)

MV: Medium Voltage.

STATCOM Unit: Static Synchronous Compensator based on Multi-Module technology and including air core reactors as needed, Valve cooling, switchgear and its control and protection.

STATCOM: Static Synchronous Compensator consisting of multiple STATCOM Units operating in parallel and connected to a common coupling Transformer. A static synchronous generator operated as a shunt connected compensator, whose capacitive or inductive output current can be controlled independently of the ac system voltage.

MSC: Mechanically Switched Capacitor (Including Switchgear). A shunt-connected circuit containing a mechanical power-switching device in series with a capacitor bank and a current limiting reactor.

MSR: Mechanically Switched Reactor (Including Switchgear). A shunt-connected circuit containing a mechanical power- switching device in series with a reactor.

Sub Module: Basic single power module of a Multi Module STATCOM unit Valve. It is a Part of a STATCOM unit valve comprising controllable switches and diodes connected in full bridge arrangement, together with their immediate auxiliaries, and storage capacitor, if any, where each controllable switch consists of one or more switched valve device(s) connected in series.

Valve: Electrically and mechanically combined assembly comprised of forced commutated devices (for example, IGBT) assembled in levels, complete with all connections, auxiliary components, and mechanical structures, which can be connected in series with each phase of reactor of a STATCOM unit.

Valve Section: Electrical assembly defined for test purposes, comprising one of several sub modules.

Valve Structure: Physical structure holding valve(s), which is insulated to the full system voltage above earth potential.

STATCOM Station: STATCOM Station includes 400 kV Switchgear, Coupling Transformer, STATCOM, MSCs (as applicable), MSRs (as applicable) along with its switchgears and complete integrated control and protection whose outputs are coordinated. (Complete turnkey delivery at site).

CT: Current Transformer.

VT: Voltage Transformer.

SAS: Substation Automation System.

Response Time: the duration from a step change in control signal until the voltage changes by 90% of its final change, before any overshoot.

Settling Time: The duration from a step change in control signal input until the STATCOM output settles to within +5% of required control output.

Slope: The ratio of the voltage change to the current change over a defined controlled range of the STATCOM, normally the full (inductive plus capacitive) range at nominal voltage, expressed as percentage.

VSC: Voltage Source Convertor, A forced commutated device (for example, IGBT) based self-commutated convertor that is capable of generating ac voltage from DC capacitor.

Voltage/Current (V/I) Characteristic: The relationship between the current of the STATCOM and the voltage at its point of connection.

Lagging Operation: Inductive operation or reactive power absorption of the STATCOM similar to a shunt reactor.

Leading Operation: Inductive operation or reactive power generation of the STATCOM similar to a shunt Capacitor.

TSP: Transmission Service Provider

- Relevant Standard:

STATCOM Station shall comply with the following standards (latest edition):

| Sl. No. | Description | Standard |
| --- | --- | --- |
|  | Voltage sourced converter (VSC) valves for STATCOM | IEC- 62927 IEEE- 1052 IEC-60747 |
|  | Control, protection & monitoring | IEC-61000 IEC-60255 |
|  | Valve Hall for housing the equipments as above comprising of: - wall bushings for connection between converter phases and decoupling reactors, - piping and tubing connections of the cooling system to converter - connection of the control cabinet with the converter through optical fibers - internal lighting, auxiliary power supply (AC and DC) and power socket system - internal HVAC system | IEC-60071 IEC-60270 IEC-60137 |
|  | X kV, dry insulated, air core and air self-cooled decoupling reactors. Mechanically Switched Reactors, half-reactors stacked on above the other, Outdoor installation, Complete with supporting structures | IEC- 60076 |
|  | Power Capacitors (MSC etc.) | IEC-60871-1 |
|  | 400 kV Power transformer (Coupling Transformer) | IEC-60076 IEC-60354 |
|  | CT’s and VT’s | IEC- 61869 |
|  | Dis-connectors and Earthing Switches | IEC- 62271 |
|  | HV & MV Circuit Breakers | IEC- 62271 |
|  | Surge Arresters | IEC- 60099 |
|  | Auxiliary & grounding transformer | IEC- 60076 IEEE C57.32 IS- 5553 (Part 6) |
|  | Neutral Grounding Resistor, charging resistor | IEEE- C57.32 |
|  | UPS, SMPS &Other Power supply units | IEC- 62040 IEC- 61558 |
|  | Others items as per relevant standards specified elsewhere in the specification for substation works. |  |
|  | Cyber Security | IEC-62243 |

- Scope of work

The scope of work with regard to the works associated with the STATCOM comprises of ±2X300 MVAr Modular Multi-level Voltage Source Converter (MMC-VSC) based STATCOM along with 4x125 MVAr MSC (Mechanically Switched Capacitors) and 2x125 MVAr MSR (Mechanically Switched Reactors). 02 Nos. STATCOM shall be distributed in two different 400 kV bus sections of the substation. The TSP shall be responsible for complete installation of STATCOM station along with the substation works as specified in the complete scope of work.

The TSP shall also perform the system studies (steady state and dynamic) according to the requirement mentioned and documentation of the same shall be preserved by TSP & to be submitted to CEA/CTU/GRID-INDIA, as per their request.

The switchgear for connection of STATCOM units, MSCs and MSRs provided on the secondary side of coupling transformer shall be of standard voltage rating as per IEC. The switchgear, structure, control, protection and substation automation on 400 kV side shall be as per applicable Technical Specification of the substation equipment.

Generally, the purpose of STATCOM is to improve system stability, provide damping, and to smooth out the step voltage change associated with MSCs, MSRs and external compensating equipment (i.e. any existing capacitor and reactor banks) switching and provide steady state VARs as needed to support the 400 kV bus voltage.

In order to get optimum control of MVAR, the control of MSCs and MSRs, as well as reactor banks connected on the 400 kV HV side, shall be integrated along with STATCOM control to provide steady state 400 kV bus voltage control in a smooth manner. MSRs and MSCs are to be switched to relieve the STATCOM from high level operation, reduce its continuous losses and maximize its dynamic control potential. The operating functions of the STATCOM Station shall include:

- Steady state voltage control of 400 kV bus,

- Balance steady state voltage at 400 kV bus,

- Dynamic over-voltage control,

- Transient and Dynamic stability control

- Damping of Power Oscillations

It is assumed that the arresters will limit any transient and switching surge over voltages and may also, by design, limit dynamic over voltages.

The requirement of reactive power compensation (as defined above) guaranteed by the TSP shall not be less than the levels specified considering following.

- The total cumulative Capacitive (+) and Inductive (-) MVAR rated Capacity of STATCOM Station as defined above comprising of STATCOM, MSCs (as applicable), MSRs (as applicable), coupling transformer, coupling reactor or any filter (if applicable) shall be rated at 1 p.u. voltage, 1 p.u. frequency and 20o Celsius ambient temperature at 400 kV Bus (Referred to as “Point of Common Coupling” or PCC).

- Capacity of one or more branches of MSC, MSR in STATCOM Station can be included in the offered STATCOM with equivalent capacity. Accordingly, ratings of STATCOM Unit/Branch equipments may be designed.

Example of equivalent acceptable solutions for each STATCOM Station is given below:

Option 1: 	±300MVAR STATCOM, 2x125MVAr Mechanically switched Shunt Capacitor (MSC), 1x125MVAr Mechanically switched Shunt Reactor (MSR).

Option 2: 	+425/-300MVAR STATCOM, 1x125MVAr Mechanically switched Shunt Capacitor (MSC), 1x125MVAr Mechanically switched Shunt Reactor (MSR).

Option 3: 	+300/-425MVAR STATCOM, 2x125MVAr Mechanically switched Shunt Capacitor (MSC).

Option 4: 	±425MVAR STATCOM, 1x125MVAr Mechanically switched Shunt Capacitor (MSC)

Option 5: 	+550/-425MVAR STATCOM

- The rated capability of STATCOM, MSC (as applicable) & MSR (as applicable) shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz.

- The STATCOM Station including STATCOM Units, MSCs and MSRs shall be designed to operate continuously under the worst possible combination of steady state voltage and frequency range of 360-440 kV and 47.5 Hz – 52 Hz respectively and transient and temporary over voltages defined in Clause 6.1-f).

- The ac voltage unbalance at fundamental frequency shall be assumed equivalent to a negative phase sequence component of 1.5 % for equipment rating purposes.

- The reactive power compensation levels shall be determined by manufacturing tolerances of the components and measurements carried out using metering accuracy instrumentation at the 400 kV feed points to the STATCOM Station.

- The reactive power capability shall also be determined by calculations based on test values of appropriate quantities at the discretion of the owner.

- In calculations of capability and availability, the owner shall assume the most unfavourable combinations of control, manufacturing and measurement tolerances.

- In case more than one STATCOM Station are installed in a particular substation, each STATCOM Station shall be connected to 400 kV bus individually with complete separate downstream system. Each individual STATCOM station shall have complete independent yet coordinated control system to avoid simultaneous tripping of both STATCOM Stations. The system shall be design in such a way that single common contingency (other than loss of 400 kV voltage, abnormal system events) will not cause tripping of both STATCOM Stations.

- Operation of STATCOM Station shall not excite any resonance condition in connected Power System.

- Control of STATCOM Station shall be designed to prevent hunting between MSRs, MSCs and STATCOM.

  - STATCOM building

The STATCOM station shall have independent building including a separate control room different from the main control room building of the Substation. The Building shall comprise of valve halls, cooling system room, control room, LT Switchgear room, Battery room, workshop, Document/Library and general facilities etc.

The STATCOM Building shall comprise of following facilities

- Control & Relay Panel room

- AC Distribution Board & DC Distribution Board room

- Battery room

- Service Room cum workshop

- Conference room

- Valve hall

- Cooling system room

- Lobby

- Corridor with minimum width of 1600 mm

- Portico

- Common Toilet

- Provision of shaft for electrical, sanitary, water supply facilities

- Other facilities as per functional requirement of building

- Air Handling Unit (AHU) Room

- Ambient Condition

STATCOM Station should be designed to perform under the ambient conditions of the site where the STATCOM is required to be installed.

- Power System Characteristic

The following AC power system characteristics apply at the point of connection i.e. point of common coupling in this case (PCC). STATCOM station operation is required within the parameter value and duration given in following table:

| S. No | Power System Characteristic | Value | unit |
| --- | --- | --- | --- |
| 1. | Nominal ac system voltage, line-to-line | 400 | kV |
| 2. | Maximum continuous ac system voltage, line-to-line | 420 | kV |
| 3. | Minimum continuous ac system voltage, line-to-line | 380 | kV |
| 4. | Maximum short-term ac system voltage, line-to-line | 448 | kV |
| 5. | Maximum duration of item 4 | 10 | s |
| 6. | Minimum short-term ac system voltage, line-to-line | 120 | kV |
| 7. | Maximum duration of item 6 | 5 | s |
| 8. | Continuous negative-sequence voltage component (used for performance calculation) | 1 | % |
| 9. | Continuous negative-sequence voltage component (used for rating calculation) | 1.5 | % |
| 10. | Continuous zero-sequence voltage component | 1 | % |
| 11. | Nominal ac system frequency | 50 | Hz |
| 12. | Maximum continuous ac system frequency | 50.5 | Hz |
| 13. | Minimum continuous ac system frequency | 48.5 | Hz |
| 14. | Maximum short-term ac system frequency | 52 | Hz |
| 15. | Minimum short-term ac system frequency | 48 | Hz |
| 16. | Basic Insulation Level (BIL) | 1550 | kV peak |
| 17. | Switching impulse level (SIL) | 1050 | kV peak |
| 18. | Power Frequency Withstand voltage | 630 | kV |
| 19. | 1) Maximum three-phase fault current a) for performance requirements b) for rating of STATCOM 2) X/R (Positive/Negative Seq) * 3) X/R (Zero Seq) * 4) Clearing time - normal 5) Clearing time – backup *Values calculated as per PSS/E study file | 1 a) 63 1 b) 63 2) 34.5 3) 8.9 4) 0.10 5) 0.75 | kA kA for 1s s s |
| 20. | Maximum three-phase fault current | 63 | kA |
| 21. | Three-phase fault current (Maximum)* *Values calculated as per PSS/E study file | 12.7 | kA |
| 22. | Minimum three-phase fault current -for performance requirements -for safe operation | 10.2 10.2 | kA kA |
| 23. | Maximum single-phase fault current | 63 | kA |
| 24. | Single-phase fault current (Maximum)* *Values calculated as per PSS/E study file | 8.8 | kA |
| 25. | Minimum single-phase fault current | 6.2 | kA |
| 26. | Power System Phase Rotation | CCW |  |

- STATCOM Station Characteristics

Figure-1: Conceptual Indicative Schematic diagram of STATCOM Station

Figure-2: VI Curve of the VSC Portion

Figure-3: VI Curve of the STATCOM Station

  - STATCOM Station Ratings

The output of a STATCOM Station shall be adjusted continuously over the range illustrated in Figure-3.

The following items define the ratings of the STATCOM station equipment.

- The STATCOM Station should regulate the 400 kV bus voltage to a reference voltage of 400 kV (1.0 per unit, Point L Figure-3), continuously adjustable between 0.95 per unit and 1.05 per unit.

- The nominal capacitive and inductive reactive power output of the STATCOM should be as defined in the scope, at 1.0 p.u. ac bus voltage and nominal system frequency, and 20°C ambient temperature (Point A and point B of figure-2).

- The slope of the STATCOM Station characteristic should be adjustable in steps of not greater than 0.5% between 1% and 8%, on a basis of cumulative MVA capacity of STATCOM Station (A+B in Figure-2).

- The STATCOM Station should continue to generate reactive power during temporary under voltage down to 120 kV (0.3 p.u.) for the duration of 5 seconds (Point C); the STATCOM system may be tripped (or blocked) if the under voltage persists for more than 5 seconds.

- The STATCOM should continue to absorb reactive power during temporary over voltages in a controlled manner as per the following.

| Temporary Overvoltage | Duration |
| --- | --- |
| up to 600kV (1.5 p.u.p.u.) | 10 seconds |
| up to 704kV (1.76 p.u.p.u.) | 100 milli seconds |
| up to 800kV (2.0 p.u.p.u.) | 50 milli seconds |

STATCOM Station may be tripped if the respective temporary over voltages as mentioned above persists for more than its respective mentioned duration.

- The STATCOM Station should be capable of repeating temporary operation as defined in any one of item (d) and (e) as above for at least 3 charging cycles in 60 minutes.

- The coupling transformer and all bus equipment, such as filter branches (if applicable), MSC & MSR branches etc. and the MV Bus should be rated to withstand the specified continuous and short-term operation, and to withstand or be protected against voltage and current stresses that exceed these conditions.

- All equipment in the STATCOM Station should be capable of sustaining, without damage, any fault limited by the maximum design short circuit level of the system and the Coupling transformer impedance.

- The TSP shall assume the negative sequence voltage of 1% at rated short circuit level and provide control to reduce this unbalance.

- The injected harmonics by STATCOM Station under the full operating range measured at 400 kV Bus (PCC) in accordance with IEEE-519-2014 and limiting values of individual harmonic distortions and total harmonic distortion shall be 0.5% and 1% respectively.

- The STATCOM controls should be designed to correct negative sequence voltage during steady state operation.

- The switching module design should include an appropriate allowance for stray capacitance and component tolerances.

- The STATCOM should be designed to prevent, or alternatively to withstand, false firing events, i.e., the firing of any valve at an incorrect time in the cycle or when not ordered.

  - Control Objectives

The control system shall control the STATCOM, MSCs, MSRs required under this specification, as well as all bus reactors on the 400 kV HV bus of the substation.

Operation logic for the breakers, disconnectors and earth-switches in the STATCOM Station shall also be incorporated in the control system. The control shall be programmable and shall have sufficient scope and flexibility (software programming margin of at least 20%) to permit re-programming according to future changes/addition in the power system. The operator interface must be integrated in a latest version of Windows environment.

    - STATCOM Station Functions and Applications

      - Voltage Control mode (Automatic and Manual)

Control of the positive sequence component of the fundamental frequency voltage in steady state and dynamic operation, with slope in the range as specified at clause 6.1 c) above

      - Fixed Reactive Power Mode

In this mode, the reactive power output of the STATCOM as well as switching of MSRs and MSCs, should be manually controlled, by direct operator action. This feature is normally utilized for testing purpose.

      - Steady State Condition

The STATCOM Station shall provide necessary reactive power support to the 400 kV bus (PCC) to compensate for voltage variation under steady state.

      - Dynamic Over-voltage Control Performance

The STATCOM shall be required to provide necessary reactive power support with fast and smooth variation so that over-voltages under dynamic conditions are controlled. STATCOM shall smooth out the step caused by switching of MSCs and MSRs.

The operation of each STATCOM over its range of MVAR from full capacitive to full inductive capacity and vice-versa shall be on the basis of smooth variation

      - Transient and Dynamic Stability Performances

The STATCOM Station shall provide necessary reactive power so that transient and dynamic stability of the Owner’s system are enhanced.

      - Damping of Power Oscillations

The STATCOM shall provide necessary damping to power oscillations by modulating its output in its entire range based on measured rate of change of power/frequency at the 400 kV bus. The damping controller would track local area oscillations as well as wide area oscillations and control would include several loops each focused on different frequency.

      - Facility for compensation of phase imbalance

Provide negative phase sequence voltage control to minimize presence of negative sequence content of the 400 kV bus voltage.

      - Start up and Initial Switching

The operation of STATCOM Station during start-up/initial switching on should not create significant energizing transients causing voltage drop, voltage distortion and swinging of transmission voltage angle at the PCC bus by more than ±5%. TSP shall have to ensure this analytically during design phase and also in the field after commissioning of the facility. TSP shall prepare the design documentation and the same shall be preserved by TSP and to be submitted to CEA/CTU/GRID-INDIA, as per their request.

      - Gain Supervision and Control

To control regulator gain in order to prevent oscillations and excessive overshoot in the STATCOM response, a gain supervision function shall be implemented.

This shall be an essential function for supervision of stability of the closed loop voltage control. The function of this controller is that when the supervision of the gain in the voltage regulator detects oscillations in the voltage controller output, the gain shall gradually be reduced until stability is reached. Normally it is a changed condition in the transmission system contribution to the closed loop gain that results in the instability. The reduction in the voltage regulator gain shall only balance the external change. The control should be adaptive in order to maximize its effectiveness. Gain reductions should be indicated and the reduction of the gain shall be able to be reset to nominal value by means of commands from the operator interface or automatically. A relative gain factor shall also be able to be changed from a gain optimizer.

      - Coordinated reactive power control of external devices

To optimize the use of dynamic vars versus steady state vars, control of externally connected shunt capacitor or reactor banks shall be implemented. Such banks will be connected locally to a HV bus or/and at MV bus. For simultaneous control with the supplementary VSC current controller, coordination for the two functions shall be provided. External devices like MSCMSR can be switched ON or OFF to position the steady state operating point of the VSC so as to extend its dynamic range.

      - Supplementary VSC current controller

To optimize the use of dynamic vars versus steady state vars, a control function that slowly reduces or offsets the STATCOM point of operation shall be implemented. By deliberately adjusting the voltage reference setting within a narrow window the STATCOM system output is pushed toward either a specific point or toward a window to preserve dynamic range. This slow operating function is meant to provide for slower controllers, such as externally connected shunt bank to operate and meet the slower long term voltage variations caused by daily or weekly load variations. Rapid changes in the system voltage that call for dynamic compensation will have priority over this type of controller.

      - Gain optimization

To provide operation at optimal regulator gain, a fully automatic optimizing function shall be implemented. This function operates by inducing a small change in the STATCOM output. The gain is adjusted based on the network response signal.

      - Control of Direct Current

During STATCOM operations, any flow of direct current to transformer MV side must be less than 25% of transformer magnetizing current. DC current flow in the transformer should be minimized by an independent control function which minimizes DC current. For presence of up to 0.2% second harmonic in 400 kV system, the STATCOM control should minimize DC current flow in the transformer.

    - Under Voltage Strategy

It is essential that the STATCOM Station operates in a robust manner when transmission system under voltages appears. For transmission system voltages down to 0.3 p.u., the STATCOM units must operate unrestricted, producing its rated capacitive current. The STATCOM must be designed to operate at transmission system under voltage, even considering that severe voltage unbalances can appear. The STATCOM must not be restricted by short term negative sequence voltages up to 1.5%, appearing in conjunction with under voltages.

Transmission system under voltages below 0.3 p.u. will appear in conjunction with transmission system faults. The STATCOM must ride through during faults and post fault under voltages. The minimum trip delay for the STATCOM Station, upon complete loss of the transmission system voltage shall not be less than 5 seconds. If station AC auxiliary power distribution is affected, critical loads must be fed from DC station batteries/UPS without tripping the STATCOM Station. Adequate capacity must be kept in DC station batteries/UPS to feed critical loads for smooth operation of the STATCOM Station facility. There must be redundant station battery system with each station battery system capable of delivering 100% load.

At under voltage conditions for the transmission system voltage, special control strategies are activated which override the normal control modes presented above. Normally if the voltage is low, the output from the STATCOM will be capacitive. If the voltage in all three phases goes below a level, but not greater than 0.3 p.u.p.u., a special under voltage strategy may be activated that controls the STATCOM output to 0 Mvar. As soon as the voltage goes higher than 0.3 p.u.p.u., the under voltage strategy is deactivated and the normal control will be in operation.

The STATCOM Station must not be tripped or shutdown automatically for under voltages appearing for less than 5 seconds. STATCOM Station must continue to operate at AC system Voltage up to 0.35 p.u.p.u.voltage on 2 phases with above 0% on the third phase or above 0.3 p.u.p.u.on all three phases until the fault is cleared and line is reclosed. The reclose time shall be up to 2.6 seconds.

    - Over Voltage Strategy

      - The TSP shall carry out dynamic stability study upfront in order to assess the dynamic overvoltage requirements. These studies shall include conditions with maximum and minimum short circuit system MVA conditions, single phase and three phase faults as well as stuck breaker, outage of nearby generator and also with outage of parts of the STATCOM Station. It is important that the STATCOM Station rides through temporary over voltages and not trip when it is needed the most.

      - The system should be able to withstand any 3 phase 5 cycle (100 ms) and single phase 10 cycles (200 ms) fault with consequent loss of a 400 kV double circuit line and loss of a 500 MW generator. The fault duration mentioned above correspond to time assumed for persistence of fault. For other system parameters refer clause 5 above (Power System Characteristics). In addition to above requirement, system contingency cases as provided in Annexure-I shall also be withstood.

      - The 400 kV system and equipment to which the STATCOM Station is connected is designed to withstand switching surge overvoltage up to 2.5 p.u. and power frequency over voltages up to 1.5 p.u. with initial value of the temporary overvoltage up to 2.0 p.u. for 1-2 cycles. Based on arrestor coordination and under the worst case scenario the 400 kV system phase to ground peak over voltages may be expected as follows:

- 650 kVp for 3 peaks

- 575 kVp up to 5 cycles

- 530 kVp up to 1 second

- 475 kVp up to 10 seconds

- The STATCOM Station shall be designed to withstand these sequential over voltages.

- If the over voltages greater than 1.1 p.u. are exceeded in magnitude and duration due to any system contingencies, suitable control action shall be taken by STATCOM Station to bear this kind of contingency.

- The TSP shall evolve the insulation co-ordination of the components of the STATCOM Station after studies have been conducted to determine the over- voltage profile with the STATCOM connected to the system.

- The TSP shall ensure that STATCOM Station will not excite ferro-resonance and sub-synchronous oscillation in the AC system. The study report in this regard shall be preserved and to be submitted to CEA/CTU/GRID-INDIA, if required.

- It may also be noted that the tripping action for 400 kV lines is initiated if the overvoltage exceeds 1.12 p.u. for 10 seconds. The tripping of 400 kV lines is initiated if 1.5 p.u. voltage persists for more than 100 milli seconds. The over voltage strategy shall be coordinated with these setting such that the STATCOM Station rides through up to these levels.

    - STATCOM Station Over load/Over Current

The overvoltage cycles mentioned in clause 6.2.3.3 above create a corresponding current overload in the STATCOM Station components; the STATCOM Station and its components shall be designed to withstand these.

In addition to the above the STATCOM Station and its components shall be designed to withstand overloading caused due to the following eventualities

- Short circuits and ground faults in the 400 kV system especially those occurring near to the STATCOM Station and medium voltage bus of the STATCOM Station.

- Transient overvoltage due to switching operations and atmospheric effects.

- Temporary over voltages.

- Short circuits in the transformer secondary circuit such as

- Bushing terminal fault

- Flashover across a reactor, Bus Bar and other connected components/switchgear etc.

- Protection system faults.

If the rated overvoltage is exceeded as a result of prolonged stressing or for other reasons, the protection specified elsewhere in the specification shall come into effect to prevent damage.

    - Dynamic Performance Controls of STATCOM Station

The TSP must describe in detail, the dynamic reactive power controls for enhancing stability margin and also damp oscillations of any critical frequencies. The dead band for continuous damping control must be very small so that there no discernible sustained oscillations.

    - Protective Control Functions

TSP shall provide all necessary protections including Main and Back-up protections for all protective zones and equipments like transformers, STATCOM Units, MSCs (if applicable), MSRs (if applicable), MV Bus Bar etc. TSP shall provide any protective control functions to meet the performance requirement of STATCOM under the scope of the TSP.

- Overvoltage Protection

TSP shall provide adequate overvoltage protection as a result of any normal operation, mal-operation or system event.

- Over current Protection

TSP shall provide adequate over-current protection for the STATCOM Station as a result of any abnormal operation, mal-operation or system event.

- Gate level control Supervision

TSP shall provide adequate Sub module Gate level control supervision.

    - STATCOM Station Response

STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30 ms of the initiating a 5% step change of voltage reference. The maximum overshoot should not exceed 120% of the total change and the settling time should not exceed 100 ms, after which the voltage should be within ±5% of the final value. This response characteristic within these limits must be respected when the system three-phase fault MVA is between the minimum and maximum value defined in clause-5. The response of the system voltage using the actual controller should be validated on a real time simulator during the Factory Acceptance Test (FAT) at the manufacturer’s premises. For the purpose of STATCOM Station response time measurement and signal conversion of the voltage, error should not exceed 0.3%. The voltage response acquisition circuit should have a response time no longer than 10 ms. However, time longer than 10 ms can be allowed provided the requirement of STATCOM response time is met.

Figure-4 Response and Settling time

  - Harmonic performance and AC harmonic filter design

It is likely that with multi-level VSC based technology, no filters or only a small high-pass filter will be needed. The STATCOM shall be operable without AC filters. The STATCOM Station should be designed to eliminate the effects of any harmonic resonance between its MSRs, MSCs banks, filters branches, and the AC system. To limit the harmonic distortion imposed on the 400 kV transmission system, additional contribution of harmonic distortion from the STATCOM Station to 400 kV system (PCC) should not exceed 1% for total and 0.5% for any specific harmonic.

    - Filter performance

The distortion levels as specified should be met for the following:

- The continuous range of all system and environmental conditions.

- Variation in total filter capacitance due to manufacturing tolerance, ambient temperature, aging and changes in capacitance up to alarm level.

- Variation in tolerance for STATCOM parameters, such as transformer winding unbalances, valve firing variations MSC and MSR unequal reactor and capacitor reactance between phases.

- System frequency in the range of 48.5 Hz to 50.5 Hz. Calculation should take into account all possible combinations of STATCOMs, MSCs and MSRs.

    - Filter component rating

The harmonic filter components (and other STATCOM components) should be rated to carry continuously the harmonic currents caused by the background harmonic distortion of the system and the harmonic currents produced by the STATCOM itself. Unless otherwise specified, harmonic currents from the system and the STATCOM of the same order should be added arithmetically. All filter harmonic currents of different order should be added quadratically (root sum of squares).

The rated voltage of capacitors should be derived from the largest arithmetic sum of the power-frequency and individual harmonic voltages obtained from stress calculations in continuous operating conditions (Note: Maximum fundamental voltage and maximum harmonic contributions may not exist at the same time for STATCOM configurations including MSRs or MSCs).

For filter capacitor voltage rating, the loss of capacitor unit or elements should be considered up to the trip level.

The rated voltage of so-called "low voltage" capacitors (e.g. in double or triple tuned filters) should be chosen such as to also withstand imposed transient stresses from faults, energization or other switching events.

    - Harmonic at PCC

The STATCOM Station contribution to the harmonic distortion levels at the STATCOM Station connection point (PCC) to the transmission system shall not exceed the limits below.

Following are the maximum limits given using denominations according to IEEE STD 519-2019. The 2nd to the 60th harmonics should be considered.

Individual harmonics voltage distortion (Dn) < or = 0.5 %

Total Harmonic voltage distortion factor (THD) < or = 1 %

    - Harmonic calculation:

Chapter 7.3 of CIGRE Publication 139 together with information in PSSE network files given shall be used for the Network harmonic impedance.

  - MV Switchyard

• 	Medium Voltage (MV) delta bus shall be grounded through a Grounding Transformer (i.e. zig-zag winding Transformer) along with suitable resistor in the neutral.

• 	MV Switchyard of different STATCOM Station branches shall be fenced with the fence height of 3 meter. Suitable arrangement i.e. electrified fence shall be done to prevent the encroachment of unwanted animal or other to minimize the probability of electrical faults (Ph-E, Ph-Ph). Further bus bar arrangement shall be made in a way to minimize the probability of electrical faults.

• 	Secondary side of the Coupling Transformer shall be provided with suitable surge capacitors to mitigate transfer surges.

• 	For MV bus bar, Aluminum conductor (Tube, Rectangular Hollow Section or C Section) may be used, however, suitable bus bar end cover/cap shall be provided to avoid any animal/bird entering the hollow space.

  - Broadband Interference

    - Radio Interference (RI)

The TSP shall take necessary precautions in the form of shielding of valve hall and building or Containers. Further, the following requirements shall also be met:

- With the STATCOM Station operating at any load upto rated value and within the design range of firing angle, the radio interference level from electromagnetic or electrostatic inductions generated by the STATCOM station shall not exceed 100 micro-volts/m, under fair weather conditions, at any point outside the station fence. The RI criteria shall be achieved at all frequencies within the range of 150 kHz to 300MHz and with the STATCOM operation at any level up to and including rated value, the design shall provide correcting measures, should the specified design not being realized in the final installation.

- Measurements of actual RI at STATCOM Station shall be made by the TSP, at points along the above defined contour and at other critical point.

- RIV (Radio Interference voltage) measured at a phase to ground voltage (266 kV rms) in accordance to NEMA-107 shall not be more than 500 micro-volts for 400 kV system. For other system voltages IEC/NEMA in the order of preference shall be applicable.

    - Interference with Power Line carrier & open wire carrier system

The TSP shall take the necessary precaution in the form of noise suppression techniques and filtering devices to prevent harmful interferences from STATCOM Station to Power Line Carrier Communication (PLCC) system operating on connected AC transmission network.

The frequency spectra to be protected are:

System 				Frequency spectrum

Power Line carrier 			30 kHz to 500 kHz

Open wire carrier 			5 kHz to 30 kHz

6.6. 	Audible Noise

The TSP shall limit the audible noise in various areas of the STATCOM Station buildings and Containers to the following values.

| Valve hall (Inside) | 90 dBA |
| --- | --- |
| Mechanical equipment areas indoor (measured at 2 metre distance) | 75 dBA |
| Mechanical equipment outdoor (Measured at 15 m distance) | 75 dBA |
| Control Room Building* | 60 dBA |
| At the limits of STATCOM STATION perimeter fence | 80 dBA |

*This is the background noise from the ventilation system adjacent rooms, control cubicles etc. Printers, recorders may be switched off during measurement.

6.7. 	Loss Requirements

6.7.1.	The TSP must guarantee the total losses of STATCOM Station, be less than 1% of the reactive power output individually at its inductive limit (STATCOM+MSRs) and capacitive limit (STATCOM+MSCs) for the cumulative highest reactive power output of STATCOM Station at PCC with worse combination of manufacturing tolerances. For the purpose of total loss measurements, it should be assumed that ambient temperature is 20°C, the PCC voltage is 1 per unit, and the slope setting is 1 %. The STATCOM system may not operate at these conditions, but they provide a common base.

6.7.2.	The total losses shall include all components, as well as different parts or subsystems of complete STATCOM Station such as coupling transformer, All VSC systems and components, MSC Capacitors and Reactors, MSR Reactors, Control and protection systems, including ancillary devices such as HMI, fault recorders, and SCADA, Auxiliary Power supply systems, cooling systems, Building ancillary services such as lighting, air conditioning, heating, and ventilation. It may be noted that for the redundant VSC valve levels and dual/redundant control and protection systems, the losses of redundant VSC valve levels and dual control and protection systems shall be considered during loss measurement.

6.7.3.	For the dual or redundant systems design of STATCOM Station, such as dual pumps or redundant fans, dual systems losses to be excluded, if the dual system is not in service during the normal operation of the STATCOM Station. However, dual systems should be included if they are required to be in service under the defined operating conditions. The same methodology shall be applied for HVAC (heating ventilation and air conditioning systems).

6.7.4.	The TSP is required to prepare documentation for the detailed calculation of total losses based on measurement during Factory Acceptance Tests of major equipment and systems mentioned above as per relevant IS/IEC/IEEE standards & same shall be preserved and to be submitted to CEA/CTU/GRID-INDIA, as per their request. Further for equipment/systems, whose loss measurement cannot be done during Factory Acceptance Test, the same can be measured at site, and a combination of calculation and measurement shall be used to derive the total losses as specified above. During Loss measurement, all fans and pumps; valve room and control room air-conditioning system shall be switched on. However, redundant fans, pumps & air-conditioners shall be kept off during loss measurement.

6.7.5.	During the factory tests the losses for the following equipment shall be measured/ assessed as detailed below:

Coupling transformer:

Losses shall be measured at factory/lab at the maximum rating, at power frequency as per relevant

IEC/IS under below conditions:

- No load loss (Iron loss) at rated voltage and fundamental frequency.

- Load loss (copper loss) at rating corresponding to maximum continuous current and at 75°C.

- Transformer cooling equipment’s loss (Auxiliary loss) at rated voltage and fundamental frequency.

Reactors:

The losses shall be measured at factory/lab at the maximum rating at power frequency as per relevant IEC/IS.

VSC Valves: Converter losses are composed of losses in power electronic switches [Insulated Gate Bipolar Transistor (IGBT) or equivalent], made up of conduction and switching losses, and the losses in DC capacitors, resistors, and inductors used within the converter system. Refer IEEE-1052 for calculating VSC losses.

Capacitor:

The capacitor losses shall be measured at manufacturer’s works at power frequency as well as calculated to obtain the losses in the complete bank on the basis of factory measurement.

Auxiliary System:

Auxiliary power losses shall be calculated from the KW and efficiency of all motors (name plate rating) of the cooling system, air conditioning, ventilation etc. The higher of the total losses for the entire auxiliary systems occurring at full capacitive capacity MVAR or full Inductive MVAR as the case may be shall be considered for arriving at the total losses.

Harmonic Filters, if any:

The losses shall be calculated at the maximum STATCOM Station loading at 400 kV and 50 Hz.

The calculations shall be on the basis of tested results of the components.

6.8. 	Selection of Insulation levels

6.8.1.	Arrestors:

Protective levels of arresters connected to the 400 kV AC Bus Bars of the STATCOM Station shall be coordinated with the insulation and surge arrester Characteristics of the 400 kV AC systems to which the STATCOM Station is to be connected. The specification and characteristics of the surge arresters installed in 400 kV AC system is given in Substation specification. The front of wave (FWWL), lightning impulse (LIWL) and switching impulse (SIWL) withstand levels shall be determined by the following margins:

- A SIWL at least 1.15 times the switching impulse protection level.

- A LIWL which is an IEC standard level corresponding to the SIWL and shall be at least 1.25 times the lightning impulse protection level.

- A FWWL which is at least 1.25 times the front of wave protection level.

In addition to above minimum basic requirement the various insulations level of 400 kV equipment shall be as below. The STATCOM Station equipment, coupling transformers etc. shall be co- ordinated accordingly.

|  | SIWL | LIWL |
| --- | --- | --- |
| All equipment including Transformer Bushing and winding | 1050 kVp | 1425 kVp |

6.8.2. 	Valves

The requirement of insulation levels of the valves shall be as per the design requirement.

6.8.3. 	Air clearances

The air clearances shall be determined by the TSP based on the required withstand levels for all waveforms in order to limit the probability of flashover within the STATCOM Station to a target value of one flashover in 15 years.

6.8.4.	Switchyard

The air clearances for switchyard equipment shall be equal to or greater than minimum values as specified in IEC-60071. Altitude correction factor (if any) shall also be considered as per IEC.

6.8.5.	Leakage distances

The Creepage/leakage distance across insulation shall be determined by the TSP and shall be adequate to ensure that under condition of heavy pollution, the probability of a flash over of an insulator does not exceed one in 15 years. However, the leakage distance for all AC insulators for outdoor installation shall not be less than 25 mm/kV of the maximum operating phase to earth rms voltage at the insulator. The leakage distance of equipment connected to 400 kV systems shall not be less than 10500 mm.

Specific creepage distance for outdoor bushings, insulator strings and long rod insulators shall be minimum 31mm/kV.

6.9. 	STATCOM Station availability and reliability

The following definitions apply:

6.9.1.	Outage terms:

- Outage

The stage in which an equipment is unavailable for normal operation due to an event directly related to the equipment which results in reduction in STATCOM Station capacity.

- Scheduled Outage

An outage which can be scheduled at least one week in advance

- Forced outage

The stage in which the equipment is unavailable for normal operation but is not in the scheduled outage stage and which results in reduction in STATCOM Station capacity i.e. an outage which is not scheduled outage.

6.9.2.	Capacity terms

Maximum Continuous Capacity (Pm)

The maximum STATCOM Station capacity (MVAR) for which continuous operation under normal condition is possible.

6.9.3.	Outage duration terms

Actual Outage Duration (AOD)

The time elapsed in hours between the start and end of an outage.

6.9.4.	Time Categories

- The number of hours in the reporting period in a full year, the period year is 8760 hours. If the equipment is commissioned, part way through a year, the period hours will be proportionately less than 8760 hours.

- Total Outage hour (TOH)

The sum of all outage duration within the reporting period. TOH = AOD

6.9.5.	Availability & Reliability Terms

Unavailability:

Unavailability is the duration for which the STATCOM Station is not available with specified rating due to forced outages per year. If part of the station is unavailable, then the unavailability duration shall be counted proportionally. However, if STATCOM is out then its duration shall count as fully unavailable STATCOM Station. However, If STATCOM unit is out then the STATCOM Station unavailability shall be counted proportionally STATCOM capacity. STATCOM Station Control system outage shall count as full STATCOM Station unavailability. ‘OF’ is the outage frequency which will be the number of forced outages per year.

The period basis for availability and reliability calculations shall be 12 months. The TSP shall ensure that the design will meet the specified guaranteed and design target value of availability and reliability.

Outage times for repair, maintenance and replacement of components shall be based on the premises that all items in the list of recommended spare parts are on hand, that all maintenance schedule of recommended maintenance are adhered to. Reliability calculations shall be made and shall be presented as the expected frequency of unscheduled loss of STATCOM Station capacity. For simultaneous occurrence of events, for either of which a loss of capacity would result, the longer repair time shall be counted.

The facilities shall be assumed to be utilized 100% of the time at 100% load, regardless of the actual reactive power generated/absorbed by the STATCOM Station. Hence the availability and reliability assessment will be based on the capability of STATCOM Station to generate/absorb the rated reactive power regardless of whether, it is in service or not.

6.9.6.	Availability Requirement

The calculated availability of the system considered on the annual basis shall be equal to or exceed the following target values.

Minimum availability requirement of each complete STATCOM Station

- Guaranteed for STATCOM Station - 98%

The outages of STATCOM Station capacity caused by the failure of equipment outside the scope of the TSP shall not be considered for calculation of availability and reliability guarantee. However, such outage shall be restricted to

- Complete loss to 400 kV supply (at PCC)

- Human Error.

Circumstances causing curtailment of STATCOM Station capacity that will be included in reliability and availability assessment and which can lead to forced outages shall include but not be limited to the following:

- Failure of equipment

- Mal-operation of control and protection system

- Failure to start

- Reduction in capacity.

6.9.7.	Reliability Requirement

- Reliability

In the assessment of reliability, the following events shall also be considered to constitute a STATCOM Station outage:

- A STATCOM Station shut down.

- A reduction of STATCOM Station capacity due to outage of any component of STATCOM Station

The calculated reliability of the complete STATCOM Station shall be equal to or exceed the following design target values.

The average outage frequency per year for each STATCOM Station shall not exceed the following values:

|  | Design target for STATCOM Station | Max acceptable Guaranteed value for STATCOM Station |
| --- | --- | --- |
| Total Numbers of Forced Outage | 3 x Nos. of STATCOM Station | 5 x Nos. of STATCOM Station |

6.9.8.	Guaranteed Failure Rate OF Sub modules (including all component and electronic): The maximum annual guaranteed failure rate of sub module (including all component and electronic) shall not exceed 1.0% per STATCOM. The failure rate shall not include failures directly attributable to operation and maintenance errors

6.9.9.	GUARANTEED OF FAILURE RATE AC POWER CAPACITOR

The maximum guaranteed annual capacitor failure rate shall not exceed 0.15% except first unit failure. The capacitor shall be considered as failed if its Capacitance value varies more than ±5% of the (actual measured) name plate value. Leakage of oil from the capacitor and deformation of the capacitor unit shall be considered as a failure even if the capacitance value is within the tolerance limits.

- Design Principles

The objective for the design of the STATCOM Station shall be to achieve high level of availability and reliability as specified. Special attention shall be given to design the STATCOM Station to avoid forced outages. The TSP shall conduct thorough design reviews to ensure minimum risk of such outages. The TSP shall give careful attention to related factors affecting STATCOM Station performance such as subsystem & system testing, protective relays co-ordination and proper setting of relays.

Except where greater reliability requirements are specified in these specifications, the design basis for STATCOM Station shall be such that no single contingency downstream from the medium voltage bus shall cause a total outage of the STATCOM Station. The following general criteria shall be followed for the design of the control system:

- Use of components similar to those whose reliability has already been proved in use.

- Use of good design practices, surge protection, filtering and interference buffers to assure Immunity to sensitive component and circuits against damage and interference by induced voltages and currents in the external cabling and cubicle wiring.

- Use of fail safe and self-checking design features.

- Use of component and equipment redundancy, by means of either duplication or triplication with automatic transfer facilities wherever necessary to meet the requirement of these specifications.

- Design which in the event of component failures, provide for transfer to a less complex operating mode.

- Provision of alarm, fault diagnosis & indication

- STATCOM Station Main Components

8.1. 	STATCOM Unit

The main electrical data of the STATCOM Units are the following:

o 	Rated voltage 					20 kV Minimum

o 	Rated frequency 					50 Hz

o 	Redundancy (Sub Module) 			2 Nos. or 5% whichever is higher

o 	Rated Power of each STATCOM unit/Branch 	50 MVAR Minimum

o 	Valve Cooling 					Deionized/Demineralized water

In general, the STATCOM units shall equally share the load however under contingency condition it should be possible to run the units with unequal load. Charging of the DC capacitors of Sub module during initial start-up shall be achieved by means of Resistors and bypass breaker arrangement. The charging resistor for DC capacitor of STATCOM Sub module should be designed for three charges per hour followed by appropriate cooling time. Power for the gate level control shall be derived internally from Sub module. The offered STATCOM Units with its Control system shall be suitably located inside the STATCOM Station Building.

8.1.1.	STATCOM Valve

The valve shall be designed to meet the performance requirements described in this specification and as described below.

In order to ensure a modern low loss and reliable solution, the STATCOM valve assembly shall use the multi-module (including redundant sub modules) approach.

The valves shall be designed to ensure satisfactory operation according to the overall performance requirements and include all necessary auxiliary equipment required for smooth and reliable operation. The valves shall be indoor air-insulated and cooled by de-mineralized water. The valves shall be of modular design and have removable Sub-Module for ease of maintenance. The valves shall be mounted to allow easy access for visual inspection, routine maintenance and replacement, and facilities shall be provided to enable the easy access.

8.1.2.	Semiconductor Switches

The electronic switches should be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. The valve shall be designed with individual semiconductor switches applied in a conservative manner with regard to their basic design parameters. The semiconductor switch shall meet the requirements of IEC 60747 except where otherwise specified herein.

The semiconductor switches shall be designed to withstand all stresses expected under steady state, transient and temporary overvoltage conditions. Basic semiconductor devices shall be of the Press Pack type, or packaged to provide short circuit means in case of device failure such that the STATCOM can continue to operate without interruption. The adjacent sub module should be protected against possible explosion of semiconductor switch.

Under the restriction of redundancy (minimum two or 5% whichever is higher) i.e. the failure of any semiconductor switch or sub module or monitoring device etc. shall not prevent continued system operation. In the event of any of the above failure, the STATCOM shall annunciate and identify the specific location of the failed device and continue operation until such time as repairs can be scheduled. During such time the next shutdown can be availed, the STATCOM must continue to operate without downgrading STATCOM capability.

The switching device’s design should include an appropriate allowance for unequal voltage distribution across individual devices in the valve due to stray capacitor and component tolerances.

The switching device’s design should include an appropriate allowance for unequal voltage distribution across individual devices in the valve due to stray capacitor and component tolerances.

Each switching device should be able to operate within component ratings, generally with at least two failed sub-module or level. The number of possible failed sub-modules or levels as specified shall be consistent with the availability requirements of the STATCOM system.

8.1.3.	Sub module for Multi-Module Topology

The key element of the Multi-Module topology shall be the Sub module. By increasing the number of these sub modules, it is possible to obtain high voltage with extremely low harmonic distortion and very low dv/dt using low switching frequency that reduces power losses. Sub module shall have the following characteristics:

VSC sub-modules should be protected against overvoltages with appropriate strategies. Description of the failure mode of the switching device and the strategies used following failure should be provided.

In each fiber optic cable (having multiple fiber cores) used for control/communication purpose of sub-module at least two fiber cores shall remain available as spare for future use.

8.1.4. 	The STATCOM sub module has DC capacitors that require a charge to allow full functionality and performance. At the startup of the STATCOM Station, the capacitors are discharged. During the energization sequence of the STATCOM, Capacitors are charged from the main power grid via resistor operated in series to the main connection circuits. Once the desired charging voltages are reached, the charging resistor circuit is bypassed using bypass switch/breaker.

The Type and Rating of the charging resistor and associated bypass switch shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station and shall conform to relevant Standard.

8.1.5.		STATCOM Valve Cooling system

A closed-loop recirculating system shall be provided with full heat rejection capacity with redundancy for pumps, heat exchangers, and fans, appropriate to the STATCOM Station availability requirements. The cooling system should be able to maintain full capacity at maximum ambient temperature and maximum STATCOM reactive power output. The cooling system should be able to operate at the lowest ambient temperature and zero output specified. The Valve cooling system shall have black start capability and necessary UPS/UMD shall be provided separately for each STATCOM Unit.

The valve cooling system shall be designed to meet the performance requirements described in this specification and as described below.

- Each STATCOM Unit shall have its own de-ionized water valve cooling system with redundant pumps.

- For cooling the STATCOM valves, a deionized re-circulating (closed loop) water system shall be used.

- Water to air heat exchanger shall be used for cooling of this de-ionized water. Water to water heat exchanger shall not be employed.

- System shall be designed such that no shut down of STATCOM be resorted to for making up the deionized water in the system. The make-up water should comply with the recommended PH and purity.

- Cooling water shall have a constant flow rate irrespective of loading. The flow rate shall be decided on the basis of extreme operating conditions.

- The control system for cooling system shall be redundant type including the provision of redundant control supply and main power supply. However, in place of redundant control system for cooling system, suitable alternate mode is also acceptable meeting the requirement of fulfilling cooling system operation even if failure of cooling control.

- 2x100% pumps with one as standby shall be provided for the primary. Should a pump failure occur, the second pump should automatically switch in without shutting down the STATCOM. An alarm shall be displayed at the control panel for failure of first pump and standby pump in operation.

- Each cooling system shall be provided with independent/dedicated UMD supply however common battery for both UMD power supply may be accepted. A UMD system will provide an extended capability of the STATCOM Station to deliver reactive power without any interruption, adding a buffer against the system faults or during events such as delayed voltage recovery or TOV.

- The secondary cooling system shall be redundant type such that it shall be possible to take out 10% (minimum one number) of the cooler module (fan unit) of secondary cooling system without affecting the rated performance of STATCOM).

- The cooling system should be designed and provided to permit work on faulty pump / faulty fan without shutting down the system.

- Normally no make-up water shall be required however in case of expansion vessel level going low; same shall be replenished automatically by means of make-up water tank and make up water pump to be supplied with the system.

- TSP shall provide water treatment plant of sufficient capacity. The purification (treatment) system shall be designed to maintain the conductivity below 1 micro siemens. A resistivity cell in the outgoing water from deionizer should detect the depletion of ionized material. Filters and deionizers shall be designed to allow replacement during operation. Normal replacement shall not be required more than once every year.

- Filters and deionizer/deoxidizer material shall be designed to allow replacement within minutes without shutdown of the cooling unit. (Normal replacement should not be required more than once/year).

- Primary cooling system shall monitor its own operation and condition of cooling water.

- The protection system of cooling cycle shall have minimum following alarms:

- Depleted deionizing cell

    - Depleted deionizing cell

    - Low water resistivity

    - High water temperature

    - Primary pump stopped

    - Fan stopped

    - Primary pump or fan interlock circuits faulty

    - Primary cycle (Make-up water) tank level low

    - Failure of control supply.

    - UMD/UPS fault.

  - Following shutdown alarms / TRIP shall be provided with cooling system protection. Excessive low water resistivity Excessive high water temperature, complete loss of auxiliary supply to primary pumps, low flow, Low Pressure etc.

  - The dissipative components of the converter are cooled with deionized water.

  - The power losses are transferred to the external ambient by means of a deionized water /air heat exchanger. All the piping and other components Complete instrumentation set has been mounted on board in order to check the status of the cooling system:

- Conductivity gauge system.

- Flow meter equipped with two set points (alarm and trip).

- Pressure meter

- Two thermometers for inlet and two thermometers for outlet (two set points for alarm and trip)

- Thermostat

  - The status of the cooling system is monitored by means of the control system.

  - Replacement of certain cooling equipment (e.g., pumps, fans, cooler unit etc.), if defective, should be possible while the cooling system still operates.

8.1.6.	Tests on STATCOM Unit Valve

All applicable tests i.e. Operational Type Tests, Dielectric Type Tests, Test for valve insensitivity to electromagnetic disturbance & Production tests shall be done as per latest edition of IEC 62927.

8.2.		STATCOM Station Control equipment and operator interface

8.2.1.	Control Equipment

The control systems should achieve the functional objectives given in Clause 6.2. The accuracy of voltage should be within ± 1% of the reference voltage. The accuracy of the gradient and linearity of the slope delivered by the STATCOM Station should be defined in relation to the current deviation from the theoretical slope defined in Clause 3.1. The maximum deviation should be less than ± 5% of nominal current.

The control system design shall be based on single fail criterion i.e. failure of any one component in the system should not result in to outage of the complete system. As a minimum, a dual (hot standby) digital programmable controller shall be supplied for each STATCOM unit/branch and STATCOM Station to control the STATCOM, MSRs and MSCs completely including the functions listed as mentioned below:

- The controller shall have diagnostic and self-checking features for both itself, and for valves, gate firing and drive circuits, interface hardware and software. This is required to reduce outage times and to facilitate fault finding.

- The Controller shall be reprogrammable. The Owner shall have at least the following possibility for changing the following reference and limit values via HMI:

- Closed loop Controllers:

The STATCOM Station controller shall have means to modify the reference set points. This refers to the functionality that will allow all the control parameters to be adjustable within selectable limits and is inclusive of, but not limited to following:

- Voltage controller

  - Q controller (reactive power controller).

o 	Supplementary VSC current controller.

o 	Other supplementary control functions.

- Sequence Controllers:

The sequence control and open-loop controllers shall include the control of all switchgears and associated control gear and external devices.

- The Controller shall have at least 10% excess I/O capacity to allow future program upgrades to satisfy the changing requirements of the power systems or future extensions to the STATCOM Stations. As a minimum a control of up to 4 future HV shunt devices (reactors or capacitors) shall be included in the offer.

- All control signals available for remote control must also be available locally so as to ensure that a local operator can operate the STATCOM Station if the communications link between STATCOM Station and remote control centers is lost.

- A changeover switch shall be provided for control the selection of local or remote control.

- Tsp shall provide the equipment necessary for the purpose of control, protection and interlocking of all equipments within the scope of supply.

- TSP shall be responsible for design and coordination of control, protection and interlocking system and switching sequences within the STATCOM Station. All necessary interfacing required between AC switchyard equipment and STATCOM Station for the above purpose shall also be included in the scope of TSP.

- It is proposed to control STATCOM through a Supervisory Control and Data Acquisition (SCADA) System. All the data shall be acquired through suitable means from field and various components and control is executed through the redundant HMI. The local STATCOM Station Control system shall consist of Redundant STATCOM Station controller, redundant HMI workstation, Gateway, STATCOM Station Control System Engineering cum Disturbance Recorder (DR), PC which can also be used as standby HMI workstations in case of emergency with associated peripheral equipment such as color laser log Printers, Color laser jet fault record printer, GPS System, Inverter / UPS etc. all interconnected via redundant Ethernet based Station LAN Network. Each work-stations and PCs at STATCOM Station shall have at least 19” LED display.

- In addition to above, HMI workstation (identical to HMI Workstation provided in STATCOM Station control room) should also be provided in control room of main 400 kV substation. This HMI workstation should be powered from an independent UPS system sufficient enough to provide power to HMI workstation for minimum two hours in case of auxiliary power failure.

- The control equipments shall satisfy the reliability and availability requirements specified in this specification

- All necessary measures shall be taken to ensure satisfactory operation in presence of harmonic current and voltage, noise and radio interference signals. The equipments shall be designed to operate in the environmental conditions specified in the specification

8.2.2.	Operator Interface

- Each STATCOM Station shall have a SCADA consisting of an HMI which shall provide a Centralized (local) operator control of the STATCOM Station functions. All human interface operations necessary for the control and monitoring of the STATCOM shall be provided at this point.

- Any abnormal condition requiring operator action or intervention or maintenance on any of the STATCOM Station subsystems shall be annunciated at the STATCOM Station control room and the Substation control room.

- The local HMI shall include the following diagrams as different screens in the display system:

  - Complete STATCOM Units and STATCOM Station single line diagram including EHV and MV busses

  - AC Auxiliary supply and distribution

  - DC Auxiliary supply and distribution

  - STATCOM Valve cooling systems

  - Interlocking system.

- These diagrams shall indicate status, alarms, voltages, currents, etc. The HMI shall provide complete diagnostics on alarm and trip indications as required and discussed in this specification, including SER information.

- A facility shall be provided whereby the local HMI features and functions shall be accessible from remote. A remote user shall be able to view screens and change STATCOM Station parameter settings.

- As Fatehgarh-3 substation where STATCOM Station shall be installed, will be equipped with Substation Automation System (SAS) conforming to IEC 61850, it is required that STATCOM Station control and monitoring shall be integrated with SAS already provided at main 400 kV Sub-station by the TSP. It is proposed to connect STATCOM Station SCADA with SAS through a Gateway and the database, configuration etc. of main substation SAS shall be upgraded to incorporate STATCOM Station events, alarms, Controls (both switchgear and control functions of STATCOM Station like setting of parameters etc.) so that STATCOM Station can be effectively monitored and controlled from main substation SAS and shall be monitored from Load Dispatch Center (NRLDC).

8.3. 	STATCOM Station Protection System

8.3.1	Protection system Design

- To ensure that faults are cleared within stability critical clearing time, to minimize damage to plant, and to avoid voltage collapse, loss of load or load limitations, TSP shall provide a high speed main protection scheme. An independent (having separate measurement system) back-up protection scheme shall be provided in the event of the main protection scheme failing or switched out for maintenance.

- The STATCOM Station shall be completely self-protecting (unit protection). STATCOM Station shall be protected from damage for all conditions of over-current, overvoltage, excessive reactive power loading, unbalance due to loss of capacitor elements, phase-to-phase and phase-to-ground faults, three phase faults, loss of cooling, semiconductor valve or control malfunction, faults (STATCOM, MV system) in individual primary connected components of the STATCOM, HV system faults, etc. The STATCOM Station shall withstand the maximum fault current for a period of the maximum fault clearing time as specified, considering second contingency cases due to the previously mentioned conditions.

- All protection equipment and systems should be properly co-ordinated to prevent incorrect operations of the protection equipment or systems during normal STATCOM Station operation, including anticipated abnormal conditions on the transmission system, as specified. Fail-safe principles should be applied throughout.

8.3.2.	The basic principle and order of precedence for the control and protection shall be, to take care of following:

  - Correctly identify a fault, problem or error condition,

  - Only if necessary, isolate the minimum number of components, subsystems whenever possible,

  - Utilize degraded modes to the maximum extent possible either directly (no interruption of the STATCOM Station operation) or indirectly (by tripping the STATCOM Station momentarily in order to isolate the branch and re-energisation of the STATCOM Station).

  - Trip STATCOM Station and Block.

- Failure of the STATCOM Station Interface (SCADA interface) shall not result in a Protection trip of the STATCOM Station. A fail-safe philosophy shall be implemented to allow the STATCOM Station to operate safely and independently from the STATCOM Station Interface (SCADA interface).

- Protection equipment shall be designed and applied to provide maximum discrimination between faulty and healthy circuits.

- The Protection shall be sufficiently sensitive to cater for the full range from maximum to minimum fault level condition. The Protection shall also be suitable for a system fault level equal to the maximum short circuit capacity of the substation. All current transformer design shall be based on these fault levels.

- All required protective, control devices, etc. including auxiliary instrument transformers and panels, relays, cabling, wiring, indication, and all other associated plant and material necessary for the effective operation of the protection systems shall be supplied and installed by TSP.

- The protective relays shall be microprocessor based. Relays shall have approved characteristics and mounted in dust and moisture proof cases. The protective relays shall be provided with visual indication for starting, tripping and failure of the protective function. The LEDs shall be reset without opening the covers. The protection relays shall also be equipped with HMI facilities suitable for manual parameter settings and viewing of the settings. Relays with provision for manual operation from outside the case, other than for resetting, are not acceptable. Relay settings shall be visible and readable without having to remove the relay cover. Relays shall be of approved construction and shall be arranged so that adjustments, testing and replacement can be effected with the minimum of time and labor. Auxiliary Relays of the hand reset type if provided shall be capable of being reset without opening the case. Electrically reset tripping relays shall be provided as necessitated by the system of control, such as for those circuits subject to remote supervisory control.

- Relay contacts shall be suitable for making and breaking the maximum currents which they may be required to control in normal service but where contacts of the protective relays are unable to deal directly with the tripping currents, approved Auxiliary tripping relays shall be provided. In such cases, the number of auxiliary tripping relays operating in tandem shall be kept to a minimum in order to achieve fast and reliable fault clearance times. Separate contacts shall be provided for alarm and tripping functions. Relay contacts shall make firmly without bounce and the whole of the relay mechanisms shall be as far as possible unaffected by vibration or external magnetic fields

- Steps shall be taken to protect the circuitry from externally impressed transient voltages which could reach the circuitry via connections to instrument transformers or the station battery. The outing of cables should be such as to limit interference to a minimum. Any auxiliary supplies necessary to power solid state circuits shall be derived from the main station battery and not from batteries internal to the protection.

- Relay communication

The Relays shall also have a communication port provided on the front of the relay for configuration and parameter settings as well as downloading of data. A direct port suitable for remote communication shall also be provided at the back of the Relay. This port shall conform to IEC - 61850.

- Tripping schemes

    - Tripping of MV circuit breakers shall be done by means of two separated trip signals.

    - Duplicate high security tripping circuits for MV Circuit Breaker shall comprise two independent high speed (less than 10 ms) high burden (greater than 150 W) tripping relays for each circuit, each with its own independent DC supply. The trip circuits for all circuit breakers need to be equipped with a “lockout” function and it shall be possible for this to be reset manually and remotely by the operator.

- The protection for the power system is based on a normal switching state and an occurrence of a single fault. This means that faults resulting from maintenance as well as the simultaneous occurrence of two or more faults are not taken into account.

- The input circuits of the digital protections shall be monitored by means of a plausibility check. If any incorrect information is found, the protection function shall be blocked by the protection. All protection relays shall have facilities for monitoring trip circuits. Detection of an interruption in the case of a switched on circuit breaker shall be signaled.

- Test facilities

    - It shall be possible to test the protective device during operation without causing trips. Links shall be provided for isolation of individual protection trip circuits and the common protection trip circuit to each circuit breaker trip coil.

    - Separate test facilities shall be provided for each current and voltage transformer secondary circuit so as to give access for testing of protection relays and associated circuits. The Test facility to be supplied shall have two selectable positions, a Service and a Test position. In the service Position, the test switch connects CTs and VTs signals to the Relays and trip commands to the circuit breaker trip coils. In the Test Position, the test switch applies a short-circuit to the CT secondary windings and open circuits the VT secondary cores and allow injection of secondary current and voltage into the relay. At the same time, the Trip commands to the Circuit Breaker Trip Coils are Isolated. The test Switch supplied shall be to the Approval of the Owner.

- The protection of the electrical system shall be designed and installed in such a way that the failed equipment is disconnected selectively and automatically. All equipment are to remain operative during transient phenomena, which may arise during switching or other disturbances to the system.

- Auxiliary DC Supplies

    - The protection concept has to be designed in a way so that back-up protection is provided at all times. All protection relays shall be configured in a way that failure of one Auxiliary DC system will not affect the relay. If all DC supplies to the controllers are lost, the STATCOM Station breaker must be tripped via the protection panel.

- Electromagnetic Compatibility

    - Electronic Relays and other electronic devices and the ancillary circuits connected to them, such as power supplies, current and voltage transformer secondaries, status or tripping or alarm circuits shall be designed to ensure that they are compatible for use in the hostile electrical environment found in an MV or HV substation.

    - Adequate steps by means of suitable design, shall be taken to prevent Electromagnetic Interference (EMI), (generated by sources such as circuit breakers, disconnectors, lightning, radio or radar emissions, switching contactors in dc circuits etc.) or Electrostatic Discharges (ESD) from affecting relay performance or causing damage to components.

    - All relays offered shall therefore have been type-tested to meet the current requirements of IEC Standards with respect to High Frequency disturbance, Fast Transients, Electrostatic Discharge, Radio Frequency Interference testing etc.

- List of Protection functions for STATCOM Station

Coupling Transformer Protection:

- Biased Differential protection (87T)

- REF protection (64T)

- Overcurrent protection (50, 51)

- Ground Overcurrent (51N)

- Overflux protection (HV and MV)

- Transformer mechanical trips

STATCOM MV Bus Protection:

- Bus Differential protection (87)

- Ground over current protection (51N), used with neutral Grounding Transformer

- Under / Over Voltage (59 Ph-Ph) protection

- Over voltage (Open Delta) protection

STATCOM Branch Protection:

- Differential protection (87)

- Overload protection (49)

- Overcurrent protection inside delta (50, 51)

- Negative phase sequence protection (46)

- STATCOM branch overcurrent protection (50, 51, 50N, 51N)

MSR Branch Protection:

- Differential protection (87)

- Ground over current protection (51N)

- Reactor branch unbalance protection (Negative Phase Sequence)

- Thermal Overload protection

MSC Branch Protection:

- Ground over current protection (51N)

- Capacitor Overvoltage (Using current signal) protection.

- Capacitor unbalance protection (60C)

- Over current protection (50, 51)

- The protection functions listed above are minimum set of function to be provided, any additional protection required to fulfill the requirement of protection system shall also be provided.

- Further protection function of individual branch (STATCOM, MSC, MSR) shall trip the respective branch MV CB.

- All CBs shall be provided with individual Breaker Failure protection relay. Breaker Failure relay shall have the logic based on current signal or CB close open status.

- Any fault on MV bus will trip the 400 kV breaker. However, any branch fault shall be cleared by respective MV branch Circuit Breaker.

- Protection System for the STATCOM valve portion of the STATCOM station shall be provided in the redundant controllers to isolate the STACOM valve during internal overload/overvoltage, ground fault etc.

8.4.	STATCOM Station Fault Recording System

An integrated Transient Fault Recording (TFR) System shall be supplied, installed & commissioned. This shall include trigger level settings for analog, etc. subject to review and comment. Disturbance and event recording facilities are required for local monitoring of the STATCOM following a disturbance on the power system or the STATCOM System. The following inputs are required:

- All analogue signals (output signals)

- All digital signals (control outputs, status indications, commands, alarms and trip indications). Internal STATCOM Station control signals/variables to be selectable.

- The accuracy of the TFR for event inputs shall be at least 100 μs (sampling rate of minimum 10 kHz).

- The TFR shall have provision for remote access and retrieval of recorded information on to a PC. For this purpose, a communication link to the Substation LAN shall be implemented.

- The remote software application for the data retrieval shall be included.

8.5.	Mechanically Switched Reactor (MSR)

MSR is a fixed source of inductive reactive power connected in shunt to the MV bus of STATCOM Station and switched by means of Circuit breaker (with control switching device) based on the command from STATCOM Station control system. The rated capability of MSRs shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz. However, The MSR Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. The individual components of MSR shall be able to withstand the onerous condition imposed by system overvoltage and harmonics. The MSR consists of 3-ph Air Core Reactor, 3-ph MV Circuit breaker (SF6/Vaccum type), associated current transformer, 3-ph Disconnector and associated safety grounding switch. The MSR area shall be fenced and castle key interlock with safety grounding switch shall be provided for human safety.

Specification for individual components like Air core reactors etc. is provided in the subsequent clause.

8.6.	Mechanically switched capacitor (MSC)

MSC is a switched 3-phase capacitor bank connected in shunt to the MV bus of STATCOM station and switched automatically by means of Circuit breaker (with control switching device) based on the command from STATCOM Station control system. The rated capability of MSCs shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz. However, TSP will ensure the corresponding values at PCC (400 kV) for possible operating condition measured at PCC. The MSC Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. The individual components of MSC shall be able to withstand the onerous condition imposed by system overvoltages and harmonics. The MSC consists of 3-ph AC power capacitor bank, current limiting air core reactor as required, 3-ph MV Circuit breaker (SF6/Vaccum type), associated current transformer, 3-ph Disconnector and associated safety grounding switch. The MSC area shall be fenced and castle key interlock with safety grounding switch shall be provided for human safety. Specification for individual components like Capacitors, Air core reactors etc. is provided in the subsequent clauses.

8.7.	Air Core Reactors

- Reactors shall be air core, dry type, be suitable for outdoor installation and there shall be no tapping on the reactors. The insulation level shall be adequate and TSP has to ensure proper insulation coordination.

- The insulation of the reactor shall be class F and hot spot temperature rise shall not exceed 105°C above ambient temperature. Winding temperature rise shall not exceed 80°C above ambient temperature.

- The reactor shall be designed to withstand thermal dynamic shocks and mechanical shocks while in service and during erection.

- The reactor shall fully conform to the relevant IEC standard.

- The reactor shall be designed to withstand overloading due to over voltage as specified and shall also be subjected to excitation by harmonics; the reactor must be able to withstand such events without deterioration in normal life.

- The reactors shall be subjected to type and routine tests in accordance with the latest issue of IEC-60076 as appropriate to the type of reactor provided.

- Tests on Reactors: The reactors shall be subjected to type and routine tests in accordance with the latest issue of IEC-60076 as appropriate to the type of reactor provided.

8.8.	AC POWER CAPACITORS

i)  	General

- The capacitor banks shall comprise of capacitor units, discharge devices, protection equipment, series reactor as required, earthing switches, suitably connected in series and parallel, mounted at ground level with protected fencing all round. The number, arrangement and connection of capacitor banks shall be designed to suit the requirement of compensator as a whole. If convenient, the capacitor banks may be used in conjunction with reactors. In this event the rating of capacitor shall be adequate to cope up with the harmonic loading. The frequency variations shall also be considered. To limit the peak in rush current for switching in the capacitors, current limiting reactors with parallel connected damping resistors if required shall be connected in series with shunt capacitor banks.

- The capacitors shall be provided with internal type fuses. Alternatively, fuseless capacitor is also acceptable.

- Fuses shall not melt nor shall deteriorate when subjected to the inrush current during the life of the bank.

- With the capacitor charged to a peak voltage, the fuses associated with the healthy elements shall not melt when carrying the discharge current resulting from a breakdown of an element or from an external short circuit.

- Fuses shall be capable of disconnecting a faulty element over a range of voltage across the unit terminals from 0.9 times rated unit voltage (Un) to 2.0 Un. In addition, if all the elements in same row of an internally fused capacitor were to fail as a result of a cascading action, the last fuse element to melt shall be capable of successful disconnection with a voltage of not less than 1.5 times.

- After fuse operation the fuse assembly shall be able to withstand continuously at least 1.5 times rated unit voltage Un across the gap for 10 Seconds.

- Fuses shall be preferably of the current limiting type but fuse system shall in any event be designed to ensure that energy released into a faulty capacitor unit is less than the valve that will cause rupture or bursting of the container.

- The capacitor units shall be outdoor type. The container of the capacitor shall be of stainless steel.

- Each capacitor unit shall be readily accessible and replaceable without disturbing any other unit. The supporting frames shall be designed to provide adequate ventilation to the units.

- The dielectric fluid used in capacitor unit shall be environmentally safe & bio-degradable, non-toxic. Polychlorinated biphenyle (PCB) type dielectric or any of its derivatives shall not be acceptable.

ii)  	Construction & Design Requirement

- The capacitors shall conform to IEC-60871. The capacitors shall be provided with internally mounted discharge resisters with characteristics in accordance with IEC-60871.

- The current limiting reactors (as required) shall be dry type and connected in series with the capacitor bank. Suitable lifting lugs shall be provided.

- The capacitor enclosure shall have sufficient strength to withstand without damage or loss of life, mechanical load, both in operation and during erection. The loads shall include electromagnetic forces including those during faults external or internal to the capacitor bank, wind loading, forces due to expansion and contraction caused by ambient temperature and load variation and seismic effects all as specified.

- The capacitor units shall be interchangeable in order to reduce the spare requirements and simplify maintenance procedures.

- The capacitor stack shall be vibration free. Stack shall have a fixed potential, that is connected to one electrical points in the bank. The stack shall be of galvanized structural steel.

- The capacitor racks shall be supplied complete with all capacitor units, insulators, and connection and shall be equipped with lifting lugs/eyes to facilitate assembly into the stacks. The racks shall be constructed of galvanized structural steel. No drilling of galvanized steel shall be allowed. Each rack shall be labeled with the weight of the fully equipped racks, the phase and bank of which it forms a part. The maximum and minimum capacitor unit capacitance which may be substituted into the racks as spares shall be suitably identified. Suitable warning labels shall be affixed.

- The capacitor shall be specially designed to be suitable for intermittent duty to which they are suitable to.

- The capacitors should comply with the overload capacity as per NEMA.

- The capacitor elements shall be vacuum dried inside the case prior to impregnation with dielectric fluid. After impregnation, the capacitor unit shall be sealed immediately upon removal of the impregnated reservoir.

- The discharge register shall discharge the unit from peak operating voltage to less than 75 Volts within 10 minutes.

- The capacitor case shall be made from type 409 stainless steel or equivalent stainless steel with all joints welded and tested for leaks.

- All racks and bus insulators as well as the insulators used to insulate each stack of capacitor from ground level shall be pincap or post type. The minimum voltage rating shall be 15 kV and low frequency wet withstand voltage of all insulator used to insulate within or between the capacitor racks of a stack shall not be less than three times the actual voltage stress across the insulators. The insulator shall be outdoor type manufactured from wet porcelain. The insulators shall be bolted to the top members of the frame to support electric grade aluminum buses.

- The size and groupings of the individual capacitor units shall be such that a single blown fuse will not cause the voltage across parallel group to rise by more than 10%.

- The redundancy to be provided, shall be as per requirement specified regarding reliability and availability in clause mentioned elsewhere.

iii)  Capacitor Unit Failure Detection

The stages of capacitor units or element failure detection shall be provided as below.

- A three-step unbalanced current protection shall be provided in each capacitor bank to initially generate an alarm when the unbalance limit is reached and finally to trip the bank in case of limit being exceeded.

- The first stage shall generate an alarm and the capacitor unit shall continue in service. It may be assumed that the bank shall be disconnected for maintenance within 2 weeks.

- The second stage shall generate a separate alarm and a delayed trip signal which will disconnect the bank after two hours.

- The third stage shall cause immediate disconnection of Capacitor Bank.

iv)  Tests on Capacitors

All the tests on capacitor units shall be generally in accordance with the latest issue of IEC publication 60871.

8.9.	Coupling Transformer

The TSP shall provide 04 Nos. single phase coupling transformer to operate as 3- ph bank with one unit as spare for stepping down the voltage from 400 kV system to a suitable medium voltage value as required. The Medium Voltage side of the coupling transformer to couple with the STATCOM shall not be less than 20 kV to ensure optimum power transformation.

The Coupling Transformer shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. The transformer should be designed & rated to carry complete capacitive and inductive reactive loading as specified for STATCOM Station including that of mechanically switched capacitor and Reactors etc.), as well as harmonic currents associated with the most onerous operating conditions of STATCOM Station, without loss of life.

The coupling transformer shall be designed in accordance with the most upto date experience in STATCOM application and shall incorporate the latest improvements of design currently employed in the industry. The Comprehensive design review of Coupling Transformer of STATCOM Station shall be carried out by the TSP.

8.9.1. 	General Requirements

The coupling transformer shall be designed electrically and mechanically for operating conditions peculiar to STATCOM Station operation, which shall include, but not be limited to the following:

- Electrical insulation problems resulting from the transformer being subjected to voltages of distorted sinusoidal wave shape because of saturation, harmonics, trapped DC in capacitors etc.

- The cumulative effect of electro-dynamic forces produced during valve commutation or other short circuit conditions imposed by valve design limitation and valve group operation.

- Harmonic currents due to STATCOM operation, with particular reference to additional stray losses resulting from these harmonic currents.

- No generation of uncharacteristic harmonics by the transformers.

- Stresses due to normal control operation and other onerous operations such as blocking and de-blocking.

- Stress due to fast response requirement of STATCOM for loading from 100% inductive to 100% capacitive and vice-versa.

- Overvoltage stresses for which STATCOM shall be designed as per specification would apply for transformer also.

- All other stresses for which STATCOM Station shall be designed as per specification would apply for transformer also.

- The transformer and all its accessories like Bushings, CTs etc. shall be designed to withstand without damage, the thermal and mechanical effects of any external short circuit to earth and of short circuit across the terminals of any winding for a period of 3 seconds. The short circuit level of 400 kV system to which the transformer shall be connected as per the maximum short circuit level of main substation. Short Circuit level of the Coupling Transformer shall be as per Short Circuit level of the respective Substation. Short circuit level for HV bushing shall be 63 kA for 1 Sec.

- The transformer shall be capable of being loaded in accordance with IEC-60076 or the overload conditions as specified which is worst. There shall be no limitation imposed by bushings during its terminal fault.

- The transformer shall be capable of withstanding the mechanical stresses caused by symmetrical or asymmetrical faults on any winding.

- The transformer should be designed to carry a certain level of direct current consistent with the STATCOM design. To ensure minimum harmonic generation, the saturation flux density of the transformer should be higher than the maximum flux density reached over the full steady state (continuous operating) range; this margin shall be at least 10%. This maximum flux density (over the full steady state range) is obtained at the highest secondary voltage during any reactive power generation, highest reference voltage, minimum slope, and minimum continuous frequency. The flux density at the highest secondary voltage shall lie in the linear portion of the B-H curve. Any harmonic generated by the transformer should be considered by the design of the STATCOM.

- All protection class Current Transformers in coupling transformer shall be of PX/PS type. Other details of these Current Transformers shall be as per protection/metering requirement and shall be decided during detailed engineering. However, the parameters of WTI Current Transformer for each winding shall be as per Coupling Transformer manufacturer.

- Transformers shall be capable of operating under natural cooled condition up to the specified load. The forced cooling equipment shall come into operation by pre-set contacts of winding temperature indicator and the transformer shall operate as a forced cooling unit initially as ONAF up to specified load and then as OFAF. Cooling shall be so designed that during total failure of power supply to cooling fans and oil pumps, the transformer shall be able to operate at full load for at least ten (10) minutes without the calculated winding hot spot temperature exceeding 140 deg C. Transformers fitted with two coolers, each capable of dissipating 50 per cent of the loss at continuous maximum rating, shall be capable of operating for 20 minutes in the event of failure of the oil circulating pump or blowers associated with one cooler without the calculated winding hot spot temperature exceeding 140 deg C at continuous max rating.

- The transformer shall be free from any electrostatic charging tendency (ECT) under all operating conditions when all oil circulation systems are in operation. In general, oil flow speed shall not exceed 1.0 m/sec within winding in the oil flow system of the transformers. The manufacturer shall ensure that there is no electrostatic charging tendency in the design.

The Technical Parameters of Transformer shall be as below

| Sl. No. | Description | Unit | Technical Parameters |
| --- | --- | --- | --- |
| 1.1 | Rated Capacity |  |  |
|  | HV | MVA | To meet the performance requirement & ratings of STATCOM. The transformer shall be suitable for 100% reactive loading |
|  | MV | MVA |  |
| 1.2 | Voltage ratio (Line to Line) |  | 400 / XX (*) |
| 1.3 | Single / Three Phase Design |  | Single phase |
| 1.4 | Applicable Standard |  | IEC 60076 |
| 1.5 | Rated Frequency | Hz | 50 |
| 1.6 | Cooling & Percentage Rating at different cooling |  | ONAN/ONAF/(OFAF or ODAF): 60% / 80%/100% OR ONAN/ONAF1/ONAF2: 60% /80%/100% OR OFAF (with 5 x 25% unit cooler if required) |
| 1.7 | Impedance at 75 Deg C |  |  |
|  | HV–MV |  | To suit the design requirements. |
| 1.8 | Tolerance on Impedance (HV-MV) | % | As per IEC |
| 1.9 | Service |  | Outdoor |
| 1.10 | Duty |  | Continuous Reactive loading |
| 1.11 | Overload Capacity |  | IEC-60076-7 |
| 1.12 | Temperature rise over 50deg C ambient Temp |  |  |
| i) | Top oil measured by thermometer | 0C | 45 |
| ii) | Average winding measured by resistance Method | 0C | 50 |
| 1.13 | Windings |  |  |
| i) | System Fault level |  |  |
|  | HV | kA | 63 |
|  | MV | kA | To suit the design requirements. |
| ii) | Lightning Impulse withstand Voltage |  |  |
|  | HV | kVp | 1300 |
|  | MV | kVp | * |
|  | Neutral | kVp | 170 |
| iii) | Switching Impulse withstand Voltage |  |  |
|  | HV | kVp | 1050 |
| iv) | One Minute Power Frequency withstand Voltage |  |  |
|  | HV | kVrms | 570 |
|  | MV | kVrms | * |
|  | Neutral | kVrms | 70 |
| v) | Neutral Grounding |  | Solidly grounded |
| vi) | Insulation |  |  |
|  | HV |  | Graded |
|  | MV |  | Uniform |
| vii) | Tan delta of winding | % | < 0.5 |
| 1.14 | Vector Group (3 – ph) (unless specified differently elsewhere) |  | YNd* |
| 1.15 | Tap Changer |  | Not Applicable |
| 1.16 | Bushing |  |  |
| i) | Rated voltage |  |  |
|  | HV | kV | 420 |
|  | MV | kV | * |
|  | Neutral | kV | 36 |
| ii) | Rated current (Min.) |  |  |
|  | HV | A | * |
|  | MV | A | * |
|  | Neutral | A | * |
| iii) | Lightning Impulse withstand Voltage |  |  |
|  | HV | kVp | 1425 |
|  | MV | kVp | * |
|  | Neutral | kVp | 170 |
| iv) | Switching Impulse withstand Voltage |  |  |
|  | HV | kVp | 1050 |
| v) | One Minute Power Frequency withstand |  |  |
|  | Voltage |  |  |
|  | HV | kVrms | 695 |
|  | MV | kVrms | * |
|  | Neutral | kVrms | 77 |
| vi) | Minimum total creepage distances |  |  |
|  | HV | mm/kV | 31mm / kV |
|  | MV | mm/kV | 31mm / kV |
|  | Neutral | mm/kV | 31mm / kV |
| vii) | Tan delta of bushings |  |  |
|  | HV | % | Refer Note 2 |
|  | MV | % | Refer Note 2 |
| viii) | Max Partial discharge level at Um |  |  |
|  | HV | pC | 10 |
|  | MV | pC | 10 |
|  | Neutral |  | - |
| 1.17 | Max Partial discharge level at 1.58 * Ur /√3 | pC | 100 |
| 1.18 | Max Noise level at rated voltage and at principal tap at no load and all cooling Active | dB | 80 |
| 1.19 | Maximum Permissible Losses of |  |  |
|  | Transformers |  |  |
| i) | Max. No Load Loss at rated voltage and Frequency | kW | To suit the design requirements. |
| ii) | Max. Load Loss at maximum continuous current and at 75O C | kW | To suit the design requirements. |
| iii) | Max. Auxiliary Loss at rated voltage and Frequency | kW | To suit the design requirements. |

Notes:

  - No external or internal Transformers / Reactors are to be used to achieve the specified HV/MV impedances.

  - The criteria for Transformer losses shall be “Copper Loss (Load Loss) > Iron Loss (No Load Loss) > Cooler Loss (Auxiliary Loss)”.

- (*) marked parameters shall be decided based on STATCOM manufacturer’s requirement

8.10. 	STATCOM Station MV Switchgear

The MV Switchgear shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station.

8.10.1. 	MV Circuit Breaker

The MV Circuit Breaker shall comply with the IEC and all other relevant Standards, and as specified in this specification. They shall satisfy the General Technical Requirements and shall be designed to operate in the environmental conditions specified in this specification.

The Circuit Breaker offered should be of SF6 type /Vacuum type only and of class C2, M2 as per IEC

- The circuit breaker shall be complete with terminal connectors, operating mechanism, control cabinets, piping, interpole cable, cable accessories like glands, terminal blocks, marking ferrules, lugs, pressure gauges, density monitors (with graduated scale), galvanised support structure for CB and control cabinets, their foundation bolts and all other circuit breaker accessories required for carrying out all the functions the CB is required to perform.

- All necessary parts to provide a complete and operable circuit breaker installation such as main equipment, terminals, control parts, connectors and other devices whether specifically called for herein or not shall be provided.

- The support structure of circuit breaker shall be hot dip galvanised. Exposed hardware items shall be hot dip galvanised or Electro-galvanised.

- MV Circuit Breaker shall be equipped with controlled switching with consequent optimization of switching behavior, when used in:

- Switching of Capacitor Bank

- Switching of shunt Reactor Bank

- Reactor Switching Duty test shall be conducted on MV Circuit Breaker in line with latest edition of IEC 62271-110.

- Type Tested for Back-to-Back Capacitor Bank Switching as per latest edition of IEC 62271-100.

- Routine tests as per IEC: 62271-100 shall be performed on all circuit breakers.

- The medium voltage circuit breakers in any of the branches shall be designed to switch off metallic three phase short circuits limited only by the transformer impedance of the STATCOM System (Coupling transformer) with the initial short circuit current and DC component according to IEC 60909-0. Thereby the worst case time constant where the maximum short circuit peak and DC component occur shall be considered. The network shall be considered to deliver the maximum short circuit power of the substation.

8.10.2. 	MV Isolator and Earth Switch

The isolators and earth switches shall comply with the IEC and all other relevant Standards, and as specified in this specification. They shall satisfy the General Technical Requirements and shall be designed to operate in the environmental conditions specified in this specification.

- The isolators and accessories shall conform in general to IEC-62271 series as per relevance (or IS:9921) except to the extent explicitly modified in specification.

- Earth switches shall be provided on isolators wherever called for.

- Switches shall be motor operated with local & remote operation feature and local manual operation feature. Remote operation of Earth Switch is not required.

- Disconnections and earth switches shall electrically and mechanically be interlocked. Castle Key interlocking facilities shall be provided to mechanically interlock the earth switch and Isolator to the doors of valve rooms.

8.10.3.	Instrument Transformers for STATCOM Station

The instrument transformers shall comply with the relevant IEC Standards. They shall satisfy the general Technical Requirement specified in specification and shall be designed to operate in the environmental conditions specified in this Specification. The instrument transformers provided for control, metering and protective relaying functions shall have voltage & current ratings, accuracy ratings and burden capabilities adequate to provide their designated functions within the overall accuracy requirement of the systems.

Voltage Transformers

Voltage transformers shall comply with the relevant IEC standards IEC 61869 (Part-1, Part-3 and Part-5).

Current Transformers

Current transformers shall comply with 61869 (Part-1 and Part-2). Type tests and routine tests as per relevant IEC.

8.10.4.	Surge Arrester

TSP shall install the surge arresters necessary for the protection of the equipment associated with STATCOM Station in accordance with the requirements as per insulation coordination study. The surge arresters shall give consistent protection to their associated equipment against overvoltages produced by lightning or switching surges, internal or external station faults, and other system disturbances.

The surge arresters shall be rated such that they are able to discharge a specified maximum energy due to the application of lightning, switching surges, temporary over voltages and faults as determined by insulation coordination studies, without coming into the temperature region where thermal runaway could result upon subsequent application of maximum transient and steady state voltage conditions.

The arrester housing shall be porcelain/composite type. The end fittings shall be made of non-magnetic and corrosion proof material.

Internal components shall be designed to eliminate internal corona and also to ensure minimal capacitive coupling with any conducting layer of pollutant on the outside of the porcelain housing Particular attention shall be given to the high discharge currents which some of the arresters may experience in service due to discharge of stored energy of the ac filter and reactive compensating equipment, tripping of STATCOM etc.

8.11. 	STATCOM Station Auxiliary Power Supply

The auxiliary supply of STATCOM Station shall conform with the system requirements relating to reliability, availability, and redundancy, performing continuously to help ensure that the complete STATCOM Station operates as per the requirements. STATCOM station Auxiliary supply including all necessary switchgear (viz. AC/DC, lighting boards etc.) shall be completely separate from the main substation auxiliary supply, all loads of STATCOM station shall be fed from this supply. The auxiliary supply provides power to the controllers, cooling system, station supplies, and various other essential and non-essential loads. With the exception of the cooling system, all other essential loads are also connected to the DC system of the STATCOM Station which is also to be provided separately from the DC system of the main substation.

The auxiliary supply system shall be able to provide a stable supply for the STATCOM Station during system faults such as single-phase faults, phase-to-phase faults, and three-phase faults and LVRT (Low Voltage Ride Through) to allow continuous operation of the STATCOM Station during these transient events.

The auxiliary supply system of each STATCOM Station shall consist of two main incomers and one emergency incomer from DG set. The two main incomers shall be required to be paired to act redundantly to help ensure a certain degree of reliability and availability. One of the main incomer shall be supplied from 33kV tertiary winding of ICT at the main substation. The other main incomer can be supplied from any one of the following three options:

- Supplied from Tertiary/Yoke winding of STATCOM coupling Transformer.

- Supplied from MV Bus Bar of STATCOM Station.

- Supplied from Power PT on HV side of coupling Transformer.

Wherever the Voltage variation on the incomer is very high, a solid state AVR (Automatic Voltage Regulator) shall be provided to control the auxiliary supply voltage.

All MV incomers shall be provided with suitable CB, disconnector, instrument Transformer etc. along with necessary protection system.

8.12. 	Fire Protection System for STATCOM Station:

Necessary fire protection for STATCOM units, Coupling Transformer, MSC, MCR and Harmonic filter (if any) shall be required. Fire-fighting system shall conform to CEA (Measures Relating to Safety & Electric Supply) Regulations.

Suitable fire detection system using smoke detectors and/or heat detectors shall be provided in STATCOM Station for all room and areas. These smoke fire detection systems shall be connected to a separate Fire annunciation system clearly identifying the zone.

The hydrant system shall be extended from fire fighting system of the substation in the yard. Suitable no. of hydrant shall be provided for protection of STATCOM Station equipment in the yard namely Coupling Transformer, MSCs, MSRs and Harmonic Filter (if required) etc. as applicable for the station. Further suitable nos. of hydrant shall also be provided for STATCOM Station building.

If HVW (High Velocity Water) Spray system is provided for transformers and reactors of main substation, the same may be extended for coupling transformer.

8.13. 	Air-conditioning and ventilation system for STATCOM station

The STATCOM Station shall be provided with Air conditioning system as per requirement.

- AC System (Except Valve Hall):

Air condition system shall be provided for the following rooms in the STATCOM Building:

  - Control and Relay room

  - Battery room

  - Conference Room

  - Store cum workshop

  - Cooling system room

  - Lobby

Capacity and quantity of the AC units shall be decided based on heat load calculation and redundancy requirement.

- Air-Conditioning System for Valve hall:

Air-Conditioning shall be provided for each Valve room for maintaining the following inside conditions round the year:

Dry Bulb Temperature (DBT): 35 oC (Maximum)

Relative Humidity (RH) - 60% (Maximum)

The system shall be designed for an outside ambient temperature of 50 oC. Based on the above system design & parameters for valve room the AC system shall comprise of “AHU & Air-cooled DX Condensing units” with one Main & one Standby unit for each room. The system shall be designed for 24 Hours, 365 Days of the year operation to maintain the inside temperatures of the Valve Hall for proper operation of the critical equipment. The air-cooled condensing unit shall be designed for continuous duty.

- Engineering studies

The TSP shall carry out studies as brought out in this section with a model of the STATCOM in PSSE and PSCAD and documentation of the same shall be preserved and to be submitted to CEA/CTU, as per their request. The objective of these studies is to verify the steady state requirement of reactive power under normal and contingent operating conditions for peak and light loads conditions in the network.

The studies shall have to be carried out for

- Peak Load

- Light Load

- Contingency Conditions

The load flow and dynamic file available with CTU shall be provided to the TSP in PSSE version 34 format. If data is not available typical data shall be assumed by TSP.

The studies should demonstrate that the STATCOM system meets all system and equipment specified performance criteria as per the specification. Engineering studies should include, but not be limited to, the studies described in subsequent subsections.

9.1. 	System dynamic performance studies

Dynamic performance studies should verify that the STATCOM system controls the system’s dynamic performance during system disturbances. Dynamic performance studies include the following:

- Studies verifying that the STATCOM provides adequate dynamic control to meet the system and STATCOM system performance criteria for the system conditions.

- Study of response time and of the STATCOM system’s behavior and contribution to the system’s recovery from faults.

- Studies to verify the operation of any supplementary controls designed to damp power oscillations following system disturbances.

- Studies to evaluate the interaction of the STATCOM controls with the other nearby control systems, including High Voltage Direct Current (HVDC) controls, generator controls, and controls of other Flexible AC Transmission System (FACTS) devices.

In addition to the above, relevant studies shall include the cases stated as mentioned in Annexure-I

9.2. 	Harmonic performance

The studies should evaluate resultant maximum harmonic levels at the STATCOM system Point of Common Coupling (PCC), and determine maximum stresses on all STATCOM system components. The study report should include the following:

- Evaluation of specified system and operating conditions (refer to Clause 5) under all possible STATCOM operating conditions.

- Evaluation within maximum ranges of STATCOM system component tolerances (worst performance values may not occur at detuning extremes).

- Evaluation with maximum system voltage unbalance (refers to item 8 and item 9 in Table 3 of Clause 5).

- Evaluation of worst case resonance condition between STATCOM system and overall system.

- Evaluation of possible resonant overvoltages.

- Transformer saturation induced harmonics for component rating calculation only.

- Evaluation of impact considering single phase auto reclose deadtime.

9.3. 	Electromagnetic transients, control performance, and overvoltage studies

Transient overvoltage studies should be performed with the actual controls modeled to verify that the STATCOM system equipment is adequately protected against overvoltages and overcurrents (including excessive valve recovery voltages) from power system transients resulting from switching, fault clearing events, and credible STATCOM system misoperations. Evaluation shall include the following:

- Study of start-up, including transformer energization, shutdown, switching coordination, and other local area network switching events

- Study of STATCOM system protection and protection coordination

- Faults on the HV and MV bus (single line-to-ground, phase-to-phase, and three-phase)

- Faults across the VSC, capacitors, and other equipment if used

- Control interaction

9.4. 	Insulation coordination study

Overall insulation coordination should be verified by considering the results of studies (dynamic overvoltages, and fault and switching transients), including the impacts of lightning surges on the STATCOM equipment. This study should determine and verify insulation levels, clearances, and arrester placement and ratings.

9.5. 	Other Studies

- Grounding Study

- Protection coordination

- PLC/radio interference

- Magnetic field strength

- Other studies as applicable

9.6. 	Software simulation models

The TSP shall provide the latest following PSCAD and PSSE simulation model(s) and parameters to CEA/CTU/GRID-INDIA alongwith detailed documentation for the purpose of future simulation to adequately represent and model the proposed STATCOM system in the respective software:

- Stability model. TSP should provide a detailed STATCOM system dynamics model for use in (PSCAD and PSSE) powerflow and stability simulation software. The model detail should be appropriate and complete for positive-sequence power system simulation and analysis that is typically performed with powerflow and transient stability programs. All appropriate control features for such analysis will be modeled, and necessary documentation on the theory and use of model should be provided. Stability model should be non-proprietary and freely available for distribution.

- Transients model. TSP should provide a detailed STATCOM transients model for use in PSCAD. The model detail should be appropriate and complete for transient response calculation of the STATCOM system. All appropriate control features for such analysis will be modeled, and necessary documentation on the theory and use of model should be provided.

  - Factory tests of controls

The integrated nature of the performance of the STATCOM in an electrical grid requires the following tests:

- The TSP should perform factory simulator system tests for integrated control and protection system to ensure the proper operation of the same. The control system should be connected to a digital simulator with adequate representation of the electrical network for various conditions. The STATCOM system controller needs to be representative of control functions, including basic controllers but inclusive of supplementary controls, firing controls, and protective functions integrated into the controllers.

- The simulator should provide an accurate network representation including network harmonic behavior, as well as synchronous condensers, power stations, generators (with AVRs), and pump storage schemes, existing HVDC, SVCs and STATCOMs, future SVCs and STATCOMs, FSC (fixed series capacitors), and shunt reactors/capacitors/filters.

STATCOM system control function type tests on a simulator should include the following:

  - Verification of each control function.

  - Verification of control linearity.

  - Verification of control redundancy.

  - Verification of the monitoring system.

  - Verification of the protection system with reference to integrated protective functions included in the Controllers and firing controllers.

  - Verification of overall system performance for minor and major system disturbances.

  - Verification of processor loading of all digital controllers.

  - Verification of STATCOM system parallel operation with other controls in the system and control Stability.

  - Verification of control equipment performance for auxiliary power supply voltage (AC and DC) and frequency variations (AC).

  - Routine production tests of all control functions, and separately of all protection functions.

  - VISUAL MONITORING SYSTEM FOR WATCH AND WARD OF             STATCOM STATION

Visual monitoring system (VMS) for effective watch and ward of STACOM station premises covering the areas of entire switchyard, STATCOM building, Coupling Transformer, Cooling Towers and main gate, shall be provided. The TSP shall design, supply, erect, test and commission the complete system including cameras, Digital video recorder system, mounting arrangement for cameras, cables, LAN Switches, UPS and any other items/accessories required to complete the system.

Features of VMS system shall be as those specified for main substation.

The number of cameras and their locations shall be decided in such a way that any location covered in the area can be scanned. The cameras shall be located in such a way to monitor at least:

- Coupling Transformer, Mechanically Switched Reactors (if any) and Mechanically Switched Capacitors (if any), AC filter banks (if any).

- STATCOM Valve hall, Cooling System, Electrical and Mechanical Auxiliary area.

- Entrance to STATCOM Station.

- All other Major Equipments (such as CB, CT, VT, SA etc.)

The cameras can be mounted on structures, buildings or any other suitable mounting arrangement.

  - Spares, Special Tools and Tackles

Considering high technology proprietary equipment of the STATCOM TSP shall ensure necessary spares are procured to maintain the necessary reliability and availability of STATCOM station. Further all necessary special tools and tackles required for erection, testing, commissioning and maintenance of equipment shall also be taken.

Annexure-I

Contingency Cases for Fatehgarh-III STATCOM

- N-1 Contingency

Contingency at 765 kV level

- Three Phase Fault close to 765 kV bus of Fatehgarh-III S/s (Section-2) followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line (1st) (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line (1st)

- Three Phase Fault close to 765 kV bus of Beawar S/s followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line (1st) (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line (1st)

- Three Phase Fault close to 765 kV bus of Beawar S/s followed by tripping of one circuit of Beawar–Dausa 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Dausa 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Dausa S/s followed by tripping of one circuit of Beawar–Dausa 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Dausa S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Dausa 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Beawar S/s followed by tripping of one circuit of Beawar–Ajmer 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Ajmer 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Ajmer S/s followed by tripping of one circuit of Beawar–Ajmer 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Ajmer S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Ajmer 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Beawar S/s followed by tripping of one circuit of Beawar– Chittorgarh 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar– Chittorgarh 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Chittorgarh S/s followed by tripping of one circuit of Beawar– Chittorgarh 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Chittorgarh S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar– Chittorgarh 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Bhadla-III S/s followed by tripping of one circuit of Ramgarh- Bhadla-III 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Ramgarh- Bhadla-III 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Ramgarh S/s followed by tripping of one circuit of Ramgarh- Bhadla-III 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Ramgarh S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Ramgarh- Bhadla-III 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Bhadla-III S/s followed by tripping of one circuit of Bhadla-III -Sikar-II 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Bhadla-III -Sikar-II 765 kV D/c line

- Three Phase Fault close to 765 kV bus of Sikar-II S/s followed by tripping of one circuit of Bhadla-III -Sikar-II 765 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 765 kV bus of Sikar-II S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Bhadla-III -Sikar-II 765 kV D/c line

Contingency at 400 kV level

- Three Phase Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1) 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1) 400 kV D/c line

- Three Phase Fault close to 400 kV bus of Fatehgarh-IV S/s (Section-1) followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1) 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Fatehgarh-IV S/s (Section-1) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1) 400 kV D/c line

- Three Phase Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line

- Three Phase Fault close to 400 kV bus of Bhadla-III S/s (Section-2) followed by tripping of one circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Bhadla-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line

- Three Phase Fault close to 400 kV bus of Beawar S/s followed by tripping of Beawar–Merta 400 kV line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Merta 400 kV line

- Three Phase Fault close to 400 kV bus of Merta S/s followed by tripping of Beawar–Merta 400 kV line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Merta S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Merta 400 kV line

- Three Phase Fault close to 400 kV bus of Beawar S/s followed by tripping of Beawar–Kota 400 kV line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Kota 400 kV line

- Three Phase Fault close to 400 kV bus of Kota S/s followed by tripping of Beawar–Kota 400 kV line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Kota S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Beawar–Kota 400 kV line

- Three Phase Fault close to 400 kV bus of Bhadla-III S/s followed by tripping of one ckt of Bhadla-III–Fatehgarh-II 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Bhadla-III–Fatehgarh-II 400 kV D/c line

- Three Phase Fault close to 400 kV bus Fatehgarh-II S/s followed by tripping of one ckt of Bhadla-III–Fatehgarh-II 400 kV D/c line (fault persist for 100 ms)

- Single Phase to Ground Fault close to 400 kV bus of Fatehgarh-II S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. tripping of one circuit of Bhadla-III–Fatehgarh-II 400 kV D/c line

Contingency at 220kV level

- Three phase fault close to 220KV Fatehgarh-III S/s (Section-2) bus with Tripping of 220KV ABC RE Solar (400MW) - Fatehgarh-III S/s (Section-2) line

- Three phase fault close to 400KV Fatehgarh-III S/s (Section-2) bus, with Tripping of 400 kV Azure Power (500MW+500MW) - Fatehgarh-III S/s (Section-2) line

- Three phase fault close to 220KV Fatehgarh-III S/s (Section-2) bus with Tripping of 220kV Adani Renewable Energy Holding Four Ltd. (300MW) - Fatehgarh-III S/s (Section-2) line

- Three phase fault close to 400KV Fatehgarh-III S/s (Section-2) bus with Tripping of 400 kV Adani Renewable Energy Holding Four Ltd. (900MW) - Fatehgarh-III S/s (Section-2) line

- Three phase fault close to 220KV Fathegarh-IV S/s (Section-1) bus with Tripping of 220kV ABC RE Solar (380MW) - Fathegarh-IV S/s (Section-1) line

- N-1-1 Contingency

Contingency at 765 kV level

- Case 1 & 2 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 3 & 4 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Fatehgarh-III S/s (Section-2) –Beawar 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 5 & 6 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar–Dausa 765 kV D/c) line and successful re-closure (dead time 1 second)

- Case 7 & 8 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Dausa S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar–Dausa 765 kV D/c) and successful re-closure (dead time 1 second)

- Case 9 & 10 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar–Ajmer 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 11 & 12 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Ajmer S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar–Ajmer 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 13 & 14 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Beawar S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar– Chittorgarh 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 15 & 16 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Chittorgarh S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Beawar– Chittorgarh 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 17 & 18 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Ramgarh- Bhadla-III 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 19 & 20 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Ramgarh S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Ramgarh- Bhadla-III 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 21 & 22 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Bhadla-III -Sikar-II 765 kV D/c line) and successful re-closure (dead time 1 second)

- Case 23 & 24 (consider as separate cases) + Single Phase Fault close to 765 kV bus of Sikar-II S/s followed by single pole opening (100 ms) of the faulted phase (2nd ckt of Bhadla-III -Sikar-II 765 kV D/c line) and successful re-closure (dead time 1 second)

Contingency at 400 kV level

- Case 25 & 26 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1)

- Case 27 & 28 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Fatehgarh-IV (Section-1) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Fatehgarh-III S/s (Section-2) –Fatehgarh-IV (Section-1)

- Case 29 & 30 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Fatehgarh-III S/s (Section-2) followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line

- Case 31 & 32 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Fatehgarh-III S/s (Section-2) –Bhadla-III 400 kV D/c line

- Case 41 & 42 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Bhadla-III S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Bhadla-III–Fatehgarh-II 400 kV D/c line

- Case 43 & 44 (consider as separate cases) + Single Phase Fault close to 400 kV bus of Fatehgarh -II S/s followed by single pole opening (100 ms) of the faulted phase and unsuccessful re-closure (dead time 1 second) followed by 3-pole opening (100 ms) of the faulted line i.e. 2nd circuit of Bhadla-III–Fatehgarh-II 400 kV D/c line

Frequently Asked Queries:

- Transmission Line:

1.1	Please clarify that whether shutdowns for crossing of existing transmission   lines of POWERGRID/STUs/ Power Evacuation Lines from Generation Plants/ Any other Transmission Licensee will be given to TSP on chargeable basis or free of cost.

Reply:	Shutdowns for crossing of existing transmission lines of POWERGRID/ STUs/ Power Evacuation Lines from Generation Plants/ Any other Transmission Licensee will be given to TSP by the concerned owner of the lines as per their own terms & conditions. As far as shutdown of ISTS lines are concerned the same can be availed by approaching respective Regional Power Committee.

1.2 	We understand that the suggested swing angle criteria are applicable for Suspension Insulator in Suspension Tower. Further, you are requested to provide similar swing angle and clearance criteria for Pilot Insulator with Jumper & Jumper.

Reply: 	It is clarified that the swing angle criteria (as mentioned in RFP) for transmission lines is applicable for Suspension Insulator in Suspension Tower. Further, as per Clause 3.0 of Specific Technical Requirements for transmission lines, Transmission service Provider (TSP) shall adopt any additional loading/design criteria for ensuring reliability of the line, if so desired and /or deemed necessary.

1.3 	We request you to kindly allow that use of diamond configuration at Power line crossings and the existing owner of the lines may be directed to allow the same for the successful bidders.

Reply:	Power line crossing including Diamond configuration is responsibility of the TSP.  TSP shall formally submit the profile of the crossing section to the owner of the existing line suggesting proposed crossing alternatives. The crossing will have to be carried out as per approval of owner of the existing line.

1.4 	It is requested you to kindly provide present status of Forest Clearances if any transmission line corridor area falling in wildlife forest / reserve forest/ mangroves.

Reply:	Based on the preliminary route survey, the process of initiation of forest clearance for the forest stretches, if any, enroute the proposed line alignment will be initiated by way of writing letters to the concerned authority (ies). However, it may be noted that it will be the responsibility of TSP for obtaining forest clearance for the forest stretches as provided in the survey report and also for any forest area encountered during detailed survey.

- Substation

2.1 	We understand that space for storage of O&M spare shall be provided by existing owner within the station boundary without any cost. Kindly confirm.

Reply:	Space for storage of O&M spares shall be arranged by TSP on its own.

2.2 	We presume that the O&M for the end Termination bays will be in the scope of the TSP and TSP shall not be liable for any payment towards O&M to the existing owner of the substation. Kindly confirm.

Reply:	Operation and maintenance of the bays is solely responsibility of the TSP.

2.3 	With reference to subject scheme of existing sub-station, we assumed following scope of work:

(a)  	We assumed internal road is available and need not to consider in the present scope of work.

(b) 	Drainage is available and need not to consider in the present scope of work.

(c) 	Cable trench extension in adjacent to Main cable trench only under present scope of work.

(d) 	Levelled area being provided by developer for bay extension.

Reply:	Regarding requirement of internal road, drainage, cable trench, leveling of the bay extension area, bidder is advised to visit site and acquaint themselves with the provisions/facilities available at substation.

2.4 	Kindly provide the soil investigation report of soil parameters of existing substation.

Reply:	Bidder is advised to visit the substation site and ascertain the requisite parameters.

2.5 	Kindly confirm, energy accounting of aux. power consumption. Whether it will be on chargeable basis or part of transmission loss.

Reply:	It will be on chargeable basis.

2.6 	We understand that VMS requirement is for unmanned stations only. For Manned stations VMS is not compulsory.

Reply:	VMS shall be provided in line with requirements of RfP document.

2.7 	It is understood that Construction water and power shall be provided free of cost to TSP by respective substation owner for construction of new bays.

Reply:	Arrangement of construction power & water is in the scope of TSP.

2.8 	It is understood that existing fire hydrant system shall be extended by the TSP for bay extension.

Reply:	Existing fire hydrant system shall be extended from existing system (if required)

2.9 	Please clarify that Status of land acquisition for Substations. Whether the lands have been acquired by BPC and will be transferred to TSP.

Reply:	The acquisition of land for substation is in the scope of TSP.

2.10 	We understood that no any dedicated metering CT & CVT required for Line/feeders. Further, we understood that requisite Energy meters for various 765kV, 400kV & 220kV Feeders shall be provided & installed by CTU free of cost to TSP.

Reply:	Dedicated metering CT and CVT are not required for line/feeders. Metering core of existing CT/CVT can be used provided accuracy class is matching with metering requirement. Requisite Special Energy Meters shall be provided and installed by CTU at the cost of TSP in C&P panel subject to space availability, else, in separate metering panel (to be provided by TSP at its cost).

- Communication

3.1 	What are the usage of OPGW, FOTE, PMU etc. under communication requirement of RFP?

Reply:	User shall be responsible for providing compatible equipment along with appropriate interface for uninterrupted communication with the concerned control center and shall be responsible for successful integration with the communication system provided by CTU.

Communication systems e.g. OPGW, FOTE, PMU etc. are required for grid operation through RLDC/SLDC, speech communication, tele-protection and tele-metering.

3.2 	Is space for installation of communication panels are provided to TSP in existing Substations incase new bays are in the scope of TSP?

Reply:	The space related issues are deliberated in the RFP itself. TSP to carry out survey of the existing substation for physical space requirement. In case space is not available in the existing substation then TSP shall accommodate the same in the respective bay SPR (Switchyard Panel Room)/Bay Kiosk/ Relay panel room in case of GIS s/s. Further, TSP to connect and integrate the proposed FOTE with the existing FOTE in the control room.

In Case 132kV Substation TSP shall accommodate the said panels either by extension of existing control room or other arrangements.

3.3 	How is the OPGW laying done in case of LILO lines?

Reply:	In case LILO lines are on same towers (e.g. both Line in and Line Out portion are on same towers, generally done LILO of S/C lines). Then 2x24F OPGW shall be required to install by TSP on both earthwire peak on 400kV & 765kV lines where two E/W peaks are available. On 220 & 132kV lines where only one E/W peak is available TSP to install one no. 48F OPGW.

Incase LILO lines are on different towers (e.g. both Line In and Line Out portion are on different towers, generally done LILO of D/C lines). Then 1x24F OPGW shall be required to install by TSP on one earthwire peak, on both Line In and Line Out portions of 400kV & 765kV lines. On 220 &132kV lines where only one E/W peak is available TSP to install one no. 24F OPGW in place of conventional earthwire.

3.4 	How is the OPGW laying done in case Multi circuit Towers?

Reply: In case two different lines are using common multi circuit portion for some distance (originating from different stations, may be terminating on same or on different stations). Two no. 24F OPGW to be installed on both E/W peaks for common M/C portion of 765kV & 400kV lines.

Incase 220/132kV lines using multi circuit portion where single E/W peak is available one no. 48F may be installed for common multi circuit portion.

Schedule: 2

Scheduled COD

[Note: As referred to in the definition of “Element”, “Scheduled COD”, and in Articles 3.1.3 (c), 4.1 (b) and 4.3 (a) of this Agreement]

| Sr. No. | Name of the Transmission Element | Scheduled COD in months from Effective Date | Percentage of Quoted Transmission Charges recoverable on Scheduled COD of the Element of the Project | Element(s) which are pre-required for declaring the commercial operation (COD) of the respective Element |
| --- | --- | --- | --- | --- |
|  | Establishment of 2x1500MVA 765/400kV Substation at suitable location near Beawar along with 2x330 MVAr 765kV Bus Reactor & 2x125 MVAr 420kV Bus Reactor | 18 months | 15.81 % | All elements of scheme marked at S. No. 1, 2, 3 and 4 are required to be commissioned simultaneously as their utilization is dependent on commissioning of each other |
|  | LILO of both circuit of Ajmer-Chittorgarh 765 kV D/c at Beawar |  | 14.10 % |  |
|  | LILO of 400kV Kota –Merta line at Beawar |  | 1.84 % |  |
|  | Fatehgarh-3 PS – Beawar 765 kV D/c along with 330 MVAr Switchable line reactor for each circuit at each end of Fatehgarh-3– Beawar 765 kV D/c line |  | 56.92 % |  |
|  | ± 2x300MVAr STATCOM, 4x125 MVAr MSC, 2x125 MVAr MSR at Fatehgarh3 PS along with 2 nos. of 400 kV bays at Fatehgarh-3 PS | 24 months | 11.33 % |  |

The payment of Transmission Charges for any Element, irrespective of its successful commissioning on or before its Scheduled COD, shall only be considered after successful commissioning of the Element(s), which are pre-required for declaring the commercial operation of such Element as mentioned in the above table.

Scheduled COD for the Project is: 24 months from Effective Date.

[Note: List of Element(s) along with the critical Element(s) to be provided by CEA]

Schedule: 3

Safety Rules and Procedures

[Note: As referred to in Articles 5.6 of this Agreement]

- Site Regulations and Safety:

### The TSP shall establish Site regulations within sixty (60) days from fulfilment of conditions subsequent, as per Prudent Utility Practices setting out the rules to be observed till expiry of the Agreement at the Site and shall comply therewith.

### Such Site regulations shall include, but shall not be limited to, rules in respect of security, safety of the Project, gate control, sanitation, medical care, and fire prevention, public health, environment protection, security of public life, etc.

Copies of such Site regulations shall be provided to the Nodal Agency and the CEA for the purpose of monitoring of the Project.

- Emergency Work:

### In cases of any emergency, the TSP shall carry out all necessary remedial work as may be necessary.

### If the work done or caused to be done by any entity, other than the TSP, the TSP shall, reimburse the actual costs incurred, to the other Party carrying out such remedial works.

- Site Clearance:

### In the course of execution of the Agreement, the TSP shall keep the Site reasonably free from all unnecessary obstruction, storage, remove any surplus materials, clear away any wreckage, rubbish and temporary works from the Site, and remove any equipment no longer required for execution of the Agreement. After completion of all Elements of the Project, the TSP shall clear away and remove all wreckage, rubbish and debris of any kind from the Site, and shall leave the Site clean and safe.

- Watching and Lighting:

### The TSP shall provide and maintain at its own expense all lighting, fencing, and watching when and where necessary for the proper construction, operation, maintenance / repair of any of the Elements of the Project, or for the safety of the owners and occupiers of adjacent property and for the safety of the public, during such maintenance / repair.

Schedule: 4

Computation of Transmission Charges

## General

The Monthly Transmission Charges to be paid to the TSP for providing Transmission Service for any Contract Year during the term of the Agreement shall be computed in accordance with this Schedule and paid as per Sharing Regulations.

Illustration regarding payment of Transmission Charges under various scenarios (considering definitions of Contract Year, Expiry Date & Monthly Transmission Charges above) is as below: -

Illustration-1:  In case the Project Elements achieve COD as per Schedule

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 28 | 1-Feb-2018 | 1-Feb-2018 | 25% |
| Element 2 | 38 | 1-Dec-2018 | 1-Dec-2018 | 75% |

Tariff Payable as follows:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Feb-18 to 31-Mar-18 | 140 X 25% X ((28+31)/365) | 5.65 |  | -- | 0.00 |
| 1-Apr-18 to 30-Nov-18 | 140 X 25% X (244/365) | 23.39 |  | -- | 0.00 |
| 1-Dec-18 to 31-Mar-19 | 140 X 100% X (121/365) |  |  |  | 46.41 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr to 30-Nov) | 140 X 100% X (244/365) |  |  |  | 93.59 |

Illustration-2: In case of extension of Scheduled COD as per Article 4.4.1 & 4.4.2 of this Agreement

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 20 | 1-Feb-2018 | 1-Jul-2018 | 25% |
| Element 2 | 28 | 1-Oct-2018 | 1-Dec-2018 | 75% |

Tariff Payable as follows:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Feb-18 to 31-Mar-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Apr-18 to 30-Jun-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Jul-18 to 30-Nov-18 | 140 X 25% X (153/365) | 14.67 |  | -- | 0.00 |
| 1-Dec-18 to 31-Mar-19 | 140 X 100% X (121/365) |  |  |  | 46.41 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr to 30-Nov) | 140 X 100% X (244/365) |  |  |  | 93.59 |

Illustration-3: In case of delay in achieving COD of Project & all individual Elements (COD of the Project achieved in Contract Year 1)

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 20 | 1-Feb-2018 | 1-Dec-2018 | 25% |
| Element 2 | 28 | 1-Oct-2018 | 1-Dec-2018 | 75% |

Tariff Payable as follows:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Feb-18 to 31-Mar-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Apr-18 to 30-Sept-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Oct-18 to 30-Nov-18 | -- | 0.00 | 1-Oct-18 to 30-Nov-18 | -- | 0.00 |
| 1-Dec-18 to 31-Mar-19 | 140 X 100% X (121/365) |  |  |  | 46.41 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr to 30-Nov) | 140 X 100% X (244/365) |  |  |  | 93.59 |

Illustration-4: In case of delay in achieving COD of Project & all individual Elements (COD of the Project achieved in Contract Year other than Contact Year 1)

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 38 | 1-Oct-2019 | 1-May-2020 | 25% |
| Element 2 | 38 | 1-Oct-2019 | 1-May-2020 | 75% |

Tariff Payment to be paid as:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Oct-19 to 31-Mar-20 | -- | 0.00 | 1-Oct-19 to 31-Mar-20 | -- | 0.00 |
| 1-Apr-20 to 30-Apr-20 | - | 0.00 | 1-Apr-20 to 30-Apr-20 | - | 0.00 |
| 1-May-20 to 31-Mar-21 | 140 X 100% X (335/365) |  |  |  | 128.49 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr to 30-Apr) | 140 X 100% X (30/ 365) |  |  |  | 11.51 |

Illustration5: In case of delay in achieving COD of Element but Project COD achieved on time

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 20 | 1-Feb-2018 | 1-Jul-2018 | 25% |
| Element 2 | 30 | 1-Dec-2018 | 1-Dec-2018 | 75% |

Tariff Payable as follows:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Feb-18 to 31-Mar-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Apr-18 to 30-Jun-18 | -- | 0.00 |  | -- | 0.00 |
| 1-Jul-18 to 30-Nov-18 | 140 X 25% X (153/365) | 14.67 |  | -- | 0.00 |
| 1-Dec-18 to 31-Mar-19 | 140 X 100% X (121/365) |  |  |  | 46.41 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr to 30-Nov) | 140 X 100% X (244/365) |  |  |  | 93.59 |

Illustration-6: In case of early commissioning of Project

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 38 | 1-Oct-2019 | 1-Jul-2019 | 25% |
| Element 2 | 38 | 1-Oct-2019 | 1-Jul-2019 | 75% |

Tariff Payment to be paid as:

| Transmission Charges for Element 1 |  | Transmission Charges for Element 2 |  |
| --- | --- | --- | --- |
| 1-July-19 to 31-Mar-20 | 140 X 100% X (274/365) |  | 105.09 |
| 2 | 140 X 100% X 1 |  | 140 |
| 3 | 140 X 100% X 1 |  | 140 |
| 4 | 140 X 100% X 1 |  | 140 |
| 5 | 140 X 100% X 1 |  | 140 |
| ……………. |  |  |  |
| …………….. |  |  |  |
| 36 (1-Apr to 30-Jun) | 140 X 100% X (91/365) |  | 34.91 |

Illustration-7: In case of early commissioning of an element

Quoted Transmission Charges: Rs. 140 Million

Completion Schedule:

| Element No. | Completion Schedule in Months | Scheduled CoD of the Element | Actual CoD of the Element | % Charges recoverable on Scheduled CoD of the Element |
| --- | --- | --- | --- | --- |
| Element 1 | 38 | 1-Oct-2019 | 1-Apr-2019 | 25% |
| Element 2 | 38 | 1-Jul-2019 | 1-Jul-2019 | 75% |

Tariff Payment to be paid as:

| Transmission Charges for Element 1 |  |  | Transmission Charges for Element 2 |  |  |
| --- | --- | --- | --- | --- | --- |
| 1-Apr-2019 to 30-Jun-19 | 140 X 25% X (91/365) | 8.72 | 1-Apr-2019 to 30-Jun-19 | -- | 0.00 |
| 1-July-19 to 31-Mar-20 | 140 X 100% X (274/ 365) |  |  |  | 105.09 |
| 2 | 140 X 100% X 1 |  |  |  | 140 |
| 3 | 140 X 100% X 1 |  |  |  | 140 |
| 4 | 140 X 100% X 1 |  |  |  | 140 |
| 5 | 140 X 100% X 1 |  |  |  | 140 |
| ……………. |  |  |  |  |  |
| …………….. |  |  |  |  |  |
| 36 (1-Apr-30-Jun) | 140 X 100% X (91/365) |  |  |  | 34.91 |

The Transmission Charges shall be payable on monthly basis as computed above.

## Computation of Monthly Transmission Charges

The Monthly Transmission Charges for any month m in a Contract Year n shall be calculated as below:

For AC System:

a. 	If Actual Transmission System Availability for the month m of contract year n is greater than or equal to 98% and less than or equal to 98.5%;

Monthly Transmission Charges MTC(m) = Tmn *1

b.	If Actual Transmission System Availability for the month m of contract year n exceeds 98.5% and less than or equal to 99.75%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 98.5%)

c.	If Actual Transmission System Availability for the month m of contract year n is greater than 99.75%;

Monthly Transmission Charges MTC(m) = Tmn * (99.75% / 98.5%)

d.	If Actual Transmission System Availability for the month m of contract year n is less than 98%and greater than or equal to 95.00%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 98%)

e.	If Actual Transmission System Availability for the month m of contract year falls below 95%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 98%) - 0.02 * (Tmn * (AA/ 95%)

For DC System:

a. 	If Actual Transmission System Availability for the month m of contract year n is greater than or equal to 95% and less than or equal to 96%;

Monthly Transmission Charges MTC(m) = Tmn *1

- If Actual Transmission System Availability for the month m of contract year n exceeds 96% and less than or equal to 99.75%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 96%)

c.	If Actual Transmission System Availability for the month m of contract year n is greater than 99.75%;

Monthly Transmission Charges MTC(m) = Tmn * (99.75% / 96%)

d.	If Actual Transmission System Availability for the month m of contract year n is less than 95% and greater than or equal to 92.00%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 95%)

e.	If Actual Transmission System Availability for the month m of contract year falls below 92%;

Monthly Transmission Charges MTC(m) = Tmn * (AA/ 95%) - 0.02 * (Tmn * (AA/ 92%)

where:

- AA is the actual Availability, as certified by RPC, as per procedure provided in Schedule 6.

- m is the month in Contract Year ‘n’

- Tmn= Transmission Charges for the month ‘m’ in Contract Year ‘n’ = (=Transmission Charge/ no. of days in the Year n) * no. of days in month m

Provided, no Transmission Charges shall be paid during the period for which the RLDC has not allowed the operation of the Element/Project due to the failure of the TSP to operate it as per the provisions of the Grid Code.

## RLDC Fee & Charges

The payment of RLDC fee & charges, in accordance with relevant regulations of CERC, shall be the responsibility of the TSP.

Schedule: 5

Quoted Transmission Charges

[Quoted Transmission Charges from Annexure - 21 of the RFP of the Selected Bidder to be inserted here]

[To be incorporated from the Bid of the Selected Bidder submitted during the e-reverse auction after its selection]

Quoted Transmission Charges: Rs. 2749.39 Million

Proportionate Transmission Charges payable for each Element of the Project:

| Sl. No. | Name of the Transmission Element | Percentage of Quoted Transmission Charges recoverable on Scheduled COD of the Element of the Project |
| --- | --- | --- |
|  | Establishment of 2x1500MVA 765/400kV Substation at suitable location near Beawar along with 2x330 MVAr 765kV Bus Reactor & 2x125 MVAr 420kV Bus Reactor | 15.81% |
|  | LILO of both circuit of Ajmer-Chittorgarh 765 kV D/c at Beawar | 14.10% |
|  | LILO of 400kV Kota –Merta line at Beawar | 1.84% |
|  | Fatehgarh-3 PS – Beawar 765 kV D/c along with 330 MVAr Switchable line reactor for each circuit at each end of Fatehgarh-3– Beawar 765 kV D/c line | 56.92% |
|  | ± 2x300MVAr STATCOM, 4x125 MVAr MSC, 2x125 MVAr MSR at Fatehgarh3 PS along with 2 nos. of 400 kV bays at Fatehgarh-3 PS | 11.33% |

Schedule: 6

Appendix II of the Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations 2019

Procedure for Calculation of Transmission System Availability Factor for a Month

- Transmission system availability factor for nth calendar month (“TAFPn”) shall be calculated by the respective transmission licensee, got verified by the concerned Regional Load Dispatch Centre (RLDC) and certified by the Member-Secretary, Regional Power Committee of the region concerned, separately for each AC and HVDC transmission system and grouped according to sharing of transmission charges. In case of AC system, transmission System Availability shall be calculated separately for each Regional Transmission System and inter-regional transmission system. In case of HVDC system, transmission System Availability shall be calculated on consolidate basis for all inter-state HVDC system.

- Transmission system availability factor for nth calendar month (“TAFPn”) shall be calculated by consider following:

- AC transmission lines: Each circuit of AC transmission line shall be considered as one element;

- Inter-Connecting Transformers (ICTs): Each ICT bank (three single phase transformer together) shall form one element;

- Static VAR Compensator (SVC): SVC along with SVC transformer shall form one element;

- Bus Reactors or Switchable line reactors: Each Bus Reactors or Switchable line reactors shall be considered as one element;

- HVDC Bi-pole links: Each pole of HVDC link along with associated equipment at both ends shall be considered as one element;

- HVDC back-to-back station: Each block of HVDC back-to-back station shall be considered as one element. If associated AC line (necessary for transfer of inter- regional power through HVDC back-to-back station) is not available, the HVDC back-to-back station block shall also be considered as unavailable;

- Static Synchronous Compensation (“STATCOM”): Each STATCOM shall be considered as separate element.

- The Availability of AC and HVDC portion of Transmission system shall be calculated by considering each category of transmission elements as under:

4. 	The availability for each category of transmission elements shall be calculated based on the weightage factor, total hours under consideration and non-available hours for each element of that category. The formulae for calculation of Availability of each category of the transmission elements are as per Appendix-III. The weightage factor for each category of transmission elements shall be considered asunder:

(a) For each circuit of AC line – Number of sub-conductors in the line multiplied by ckt-km;

(b) For each HVDC pole- The rated MW capacity x ckt-km;

(c) For each ICT bank – The rated MVA capacity;

(d) For SVC- The rated MVAR capacity (inductive and capacitive);

(e) For Bus Reactor/switchable line reactors – The rated MVAR capacity;

(f) For HVDC back-to-back station connecting two Regional grids- Rated MW capacity of each block; and

(g) For STATCOM – Total rated MVAR Capacity.

5. 	The transmission elements under outage due to following reasons shall be deemed to be available:

i. 	Shut down availed for maintenance of another transmission scheme or construction of new element or renovation/upgradation/additional capitalization in existing system approved by the Commission. If the other transmission scheme belongs to the transmission licensee, the Member Secretary, RPC may restrict the deemed availability period to that considered reasonable by him for the work involved. In case of dispute regarding deemed availability, the matter may be referred to Chairperson, CEA within 30 days.

ii. 	Switching off of a transmission line to restrict over voltage and manual tripping of switched reactors as per the directions of concerned RLDC.

6. 	For the following contingencies, outage period of transmission elements, as certified by the Member Secretary, RPC, shall be excluded from the total time of the element under period of consideration for the following contingencies:

i) Outage of elements due to acts of God and force majeure events beyond the control of the transmission licensee. However, whether the same outage is due to force majeure (not design failure) will be verified by the Member Secretary, RPC.A reasonable restoration time for the element shall be considered by Member Secretary, RPC and any additional time taken by the transmission licensee for restoration of the element beyond the reasonable time shall be treated as outage time attributable to the transmission licensee. Member Secretary, RPC may consult the transmission licensee or any expert for estimation of reasonable restoration time. Circuits restored through ERS (Emergency Restoration System) shall be considered as available;

ii) Outage caused by grid incident/disturbance not attributable to the transmission licensee, e.g. faults in substation or bays owned by other agency causing outage of the transmission licensee’s elements, and tripping of lines, ICTs, HVDC, etc. due to grid disturbance. However, if the element is not restored on receipt of direction from RLDC while normalizing the system following grid incident/disturbance within reasonable time, the element will be considered not available for the period of outage after issuance of RLDC’s direction for restoration;

Provided that in case of any disagreement with the transmission licensee regarding reason for outage, same may be referred to Chairperson, CEA within 30 days. The above need to be resolved within two months:

Provided further that where there is a difficulty or delay beyond sixty days, from the incidence in finalizing the recommendation, the Member Secretary of concerned RPC shall allow the outage hours on provisional basis till the final view.

7. Time frame for certification of transmission system availability: (1) Following schedule shall be followed for certification of availability by Member Secretary of concerned RPC:

- Submission of outage data by Transmission Licensees to RLDC/ constituents

  - By 5th of the following month;

- Review of the outage data by RLDC / constituents and forward the same to respective RPC – by 20th of the month;

- Issue of availability certificate by respective RPC – by 3rd of the next month.

Schedule: 7

Entire Bid (both financial bid and technical bid) of the Selected Bidder to be attached here

Schedule: 8

Contract Performance Guarantee

(To be on non-judicial stamp paper of appropriate value as per Stamp Act relevant to place of execution. Foreign entities submitting Bids are required to follow the applicable law in their country.)

In consideration of the ……………………..[Insert name of the SPV or Selected Bidder on behalf of the TSP, or Lead Member in case of the Consortium, with address] agreeing to undertake the obligations under the Transmission Service Agreement dated ……….and the other RFP Project Documents and the Nodal Agency and the ……………………..[Insert the name of the BPC], agreeing to execute the RFP Project Documents with the Selected Bidder, regarding setting up the Project, the ………………………………. [Insert name and address of the bank issuing the guarantee and address of the head office] (hereinafter referred to as “Guarantor Bank”) hereby agrees unequivocally, irrevocably and unconditionally to pay to …………… (being the Nodal Agency) at ……………………[Insert the Place from the address of the Nodal Agency indicated in the TSA] forthwith on demand in writing from the Nodal Agency or any Officer authorized by it in this behalf, any amount up to and not exceeding Rupees ………………………….. Crores (Rs. ……….) only [Insert the amount of the bank guarantee] on behalf of M/s. …………………………………. [Insert name of the Selected Bidder or SPV].

This guarantee shall be valid and binding on the Guarantor Bank up to and including ……………………….and shall not be terminable by notice or any change in the constitution of the Bank or the term of the Transmission Service Agreement or by any other reasons whatsoever and our liability hereunder shall not be impaired or discharged by any extension of time or variations or alternations made, given, or agreed with or without our knowledge or consent, by or between parties to the respective agreement.

Our liability under this Guarantee is restricted to Rs. ………………….. Crores (Rs. ……………………………..) only. Our Guarantee shall remain in force until ……………………………………….. [Insert the date of validity of the Guarantee as per Article 3.1.2 of this Agreement]. The Nodal Agency, shall be entitled to invoke this Guarantee up to three hundred sixty-five (365) days of the last date of the validity of this Guarantee.

The Guarantor Bank hereby expressly agrees that it shall not require any proof in addition to the written demand from …………… (in its roles as the Nodal Agency), made in any format, raised at the above mentioned address of the Guarantor Bank, in order to make the said payment to Nodal Agency.

The Guarantor Bank shall make payment hereunder on first demand without restriction or conditions and notwithstanding any objection by ...................................... [Insert name of the Selected Bidder], ……………………….. [Insert name of the TSP] and / or any other person. The Guarantor Bank shall not require Nodal Agency to justify the invocation of this BANK GUARANTEE, nor shall the Guarantor Bank have any recourse against Nodal Agency in respect of any payment made hereunder.

THIS BANK GUARANTEE shall be interpreted in accordance with the laws of India.

The Guarantor Bank represents that this BANK GUARANTEE has been established in such form and with such content that it is fully enforceable in accordance with its terms as against the Guarantor Bank in the manner provided herein.

THIS BANK GUARANTEE shall not be affected in any manner by reason of merger, amalgamation, restructuring, liquidation, winding up, dissolution or any other change in the constitution of the Guarantor Bank.

THIS BANK GUARANTEE shall be a primary obligation of the Guarantor Bank and accordingly Nodal Agency shall not be obliged before enforcing this BANK GUARANTEE to take any action in any court or arbitral proceedings against …………………… [Insert name of the SPV] or the Selected Bidder, as the case may be, to make any claim against or any demand on …………………… [Insert name of the SPV] or the Selected Bidder, as the case may be, or to give any notice to …………………… [Insert name of the SPV] or the Selected Bidder, as the case may be, or to enforce any security held by the Nodal Agency or to exercise, levy or enforce any distress, diligence or other process against …………………… [Insert name of the SPV] or the Selected Bidder, as the case may be.

The Guarantor Bank acknowledges that this BANK GUARANTEE is not personal to Nodal Agency and may be assigned, in whole or in part, (whether absolutely or by way of security) by Nodal Agency to any entity to whom the Nodal Agency is entitled to assign its rights and obligations under the Transmission Service Agreement.

The Guarantor Bank hereby agrees and acknowledges that Nodal Agency shall have a right to invoke this Bank Guarantee either in part or in full, as it may deem fit.

Notwithstanding anything contained hereinabove, our liability under this Guarantee is restricted to Rs. ………………….. Crores (Rs. …………………..) only and it shall remain in force until ………………………[Date to be inserted on the basis of Article 3.1.2of the Transmission Service Agreement], with an additional claim period of three hundred sixty five (365) days thereafter. This BANK GUARANTEE shall be extended from time to time for such period, as may be desired by …………………………………….. [Insert name of the Selected Bidder or Lead Member in case of the Consortium or SPV]. We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only if Nodal Agency serves upon us a written claim or demand.

In witness where of:

Signature ..............................................

Name: ...................................................

Power of attorney No.: ………………………………

For:

………………………………….. [Insert Name of the Bank]

Banker's Seal and Full Address, including mailing address of the Head Office

Schedule: 9

Methodology for determining the Relief Under Force Majeure Event & Change in Law during Construction Period

The relief in the form of revision in tariff due to Force Majeure Event leading to extension of Scheduled COD for a period beyond one hundred eighty (180) days and/ or Change in Law during the construction period shall be as under:

ΔT = [(P x d)]÷[1-(1+ d)^(-n)]

Where,

ΔT = Change in Transmission Charges for each year

P = Sum of cumulative increase or decrease in the cost of the Project due to Change in Law and interest cost during construction corresponding to the period exceeding one hundred eighty (180) due to Force Majeure Event leading to extension of Scheduled COD for a period beyond one hundred eighty (180) days

n = number of years over which the Transmission Charges has to be paid

d = 7.70 % (Discount rate as notified by the CERC, applicable on the Bid Deadline as per CERC notification dated 06.04.2023).

The increase in Transmission Charges as stated above shall be applicable only if the value of increase in Transmission Charges as calculated above exceeds 0.30% (zero point three percent) of the quoted Transmission Charges of the TSP.